## ML Models
BESS Machine-Learning Models — Objectives, Models & Input Data
# | Category | Use Case | Objective | ML Task | Model(s) Used | Input Datasets | Input Data / Features → Target | Feasibility
1 | Battery health & safety | State of Health (SOH) estimation | Track usable-capacity fade to schedule augmentation and honour warranties. | Regression | LightGBM / XGBoost, LSTM | BMS, Module | cell V/T envelope, imbalance, cycles, throughput, calendar age → SOH % | Ready
2 | Battery health & safety | Remaining Useful Life (RUL) | Predict time/cycles to end-of-life for replacement planning. | Survival / Regression | Weibull AFT, DeepSurv, GRU | BMS, Module | degradation trajectory + usage → cycles/days to EOL | Needs field data
3 | Battery health & safety | SOC estimation / correction | Sharper state-of-charge than coulomb counting alone, resists drift. | Regression (state est.) | EKF/UKF hybrid, NN, TCN | BMS | pack V, current, temperature → true SOC % | Partial
4 | Battery health & safety | Internal-resistance / impedance soft sensor | Estimate cell resistance (an ageing marker) without an EIS test. | Regression | Ridge, GBM, physics-informed NN | BMS | V response to current steps, temp → R_internal | Partial
5 | Battery health & safety | Weak-cell / module outlier detection | Flag modules drifting from the pack before they force a derate. | Anomaly / Clustering | Isolation Forest, DBSCAN, z-score | Module | per-module V/T deviation vs pack → outlier score | Ready
6 | Battery health & safety | Thermal-runaway early warning | Detect the pre-runaway signature (venting, dV/dt, dT/dt) early. | Classification / Anomaly | 1D-CNN, autoencoder + threshold | BMS, Module, HVAC | cell V/T rates, imbalance, gas (if any) → risk flag | Needs field data
7 | Battery health & safety | Capacity-fade forecasting | Project the SOH curve months ahead under a usage plan. | Time-series regression | Prophet, N-BEATS, Gaussian Process | BMS | daily SOH history + operating profile → future SOH | Needs field data
8 | Anomaly & fault detection | Multivariate anomaly detection | One model that flags 'this doesn't look like normal operation'. | Unsupervised | Autoencoder, Isolation Forest, One-Class SVM | BMS, PCS, HVAC, EMS | joined 5-min telemetry → reconstruction / density score | Ready
9 | Anomaly & fault detection | Fault classification / diagnosis | Name the fault type from the telemetry signature. | Supervised classification | GBM, 1D-CNN, Random Forest | BMS, PCS, HVAC, Alarms | telemetry window + alarm labels → fault class | Partial
10 | Anomaly & fault detection | Alarm / fault prediction (early warning) | Predict an alarm N steps before it trips, to act pre-emptively. | Classification (horizon) | LSTM, Temporal CNN, GBM | BMS, PCS, HVAC, Alarms | recent telemetry → P(alarm within Δt) | Partial
11 | Anomaly & fault detection | Alarm correlation & root-cause | Group co-occurring alarms and point to the originating asset. | Association / Graph | FP-growth, Bayesian nets, GNN | Alarms, Dispatch | alarm sequences + asset topology → cause ranking | Partial
12 | Anomaly & fault detection | Alarm-flood reduction / de-duplication | Collapse alarm storms into a few actionable events. | Sequence clustering | Sequence clustering, LSTM-AE | Alarms | alarm stream → clustered incidents | Ready
13 | Anomaly & fault detection | Sensor drift & data-quality detection | Spot stuck/drifting sensors and fill gaps before they poison models. | Anomaly + imputation | Kalman, matrix factorisation, KNN-impute | BMS, PCS, HVAC, EMS | per-signal residuals vs peers → drift flag + imputed value | Ready
14 | Forecasting | Electricity-price forecasting | Feed the arbitrage optimiser with a day-ahead / intraday price curve. | Time-series | LightGBM, N-BEATS, Temporal Fusion Transformer | EMS | price history + calendar/TOU → future price | Ready
15 | Forecasting | SOC-trajectory forecasting | Anticipate available energy for the next dispatch window. | Time-series | LSTM, seq2seq, GBM | BMS, EMS, Dispatch | SOC + planned dispatch → future SOC | Ready
16 | Forecasting | Temperature forecasting | Predict cell / IGBT / coolant temps to pre-cool and avoid derates. | Time-series regression | TCN, LSTM, GBM | BMS, PCS, HVAC | load, ambient, cooling state → future temperature | Ready
17 | Forecasting | Net-load & demand / peak forecasting | Forecast site load & peaks for peak-shaving and capacity commitments. | Time-series | Prophet, TFT, GBM | EMS | historical load, weather, calendar → load / peak | Partial
18 | Forecasting | Auxiliary / HVAC energy forecasting | Predict parasitic draw to net it out of dispatch economics. | Time-series regression | GBM, LSTM | HVAC, EMS | ambient, load, cooling mode → aux kW | Ready
19 | Optimization & control | Energy-arbitrage / dispatch optimization | Buy-low/sell-high to maximise revenue under SOC & power limits. | RL / MPC surrogate | DQN/PPO, stochastic MPC, imitation of EMS | EMS, Dispatch | price forecast, SOC, limits → charge/discharge setpoint | Partial
20 | Optimization & control | Dispatch imitation learning | Learn the EMS's own policy as a fast, deployable surrogate. | Imitation / Supervised | Behaviour cloning (GBM/NN) | EMS, Dispatch | state (price, SOC, time) → EMS action | Ready
21 | Optimization & control | Frequency-regulation response & bidding | Track AGC accurately and size FR bids for revenue vs wear. | RL / Control | PPO, LQR, MPC | EMS, PCS | frequency, AGC signal, SOC → power response / bid | Partial
22 | Optimization & control | Optimal market bidding | Place energy/ancillary bids under price & availability uncertainty. | Stochastic opt / RL | SDDP, RL, scenario optimisation | EMS, Dispatch | price scenarios, availability → bid curve | Partial
23 | Optimization & control | Degradation-aware dispatch | Trade a little revenue for less ageing using an SOH model in the reward. | RL (multi-objective) | Constrained RL, MPC + ageing model | EMS, BMS, Dispatch | state + SOH-cost model → dispatch | Partial
24 | Optimization & control | Predictive / optimal thermal control | Minimise HVAC energy while holding temperature within limits. | RL / MPC | MPC, PPO, contextual bandit | HVAC, BMS | heat load, ambient, temps → setpoint / compressor cmd | Ready
25 | Optimization & control | Volt-VAR / reactive-power optimization | Provide voltage support within the kVA circle at least cost. | Optimization | Convex opt, RL | PCS, EMS | POI voltage, P, limits → Q setpoint | Partial
26 | Efficiency & performance | Round-trip / PCS efficiency modeling | Model efficiency vs load/SOC/temp to benchmark and detect decline. | Regression | GBM, GAM, polynomial | PCS, EMS | load, SOC, temperature → efficiency % | Ready
27 | Efficiency & performance | HVAC COP & cooling-performance modeling | Model coefficient-of-performance to tune control and catch fouling. | Regression | GBM, GAM | HVAC | ambient, load, compressor → COP | Ready
28 | Efficiency & performance | Loss decomposition / performance benchmarking | Attribute losses (cell, PCS, aux) and rank units against peers. | Regression / analytics | Regression, SHAP attribution | BMS, PCS, HVAC, EMS | energy in/out by stage → loss breakdown | Ready
29 | Efficiency & performance | Heat-load prediction (thermal design) | Predict battery+PE heat into the loop for cooling sizing/control. | Regression | GBM, physics-informed | BMS, PCS, HVAC | power, C-rate, ambient → heat load kW | Ready
30 | Reliability, O&M & economics | Predictive maintenance (component) | Anticipate compressor, fan, contactor or IGBT failures. | Classification / RUL | Survival models, GBM, LSTM | HVAC, PCS, Alarms | component signals + service history → failure risk | Needs field data
31 | Reliability, O&M & economics | Dispatch-adherence / tracking anomaly | Detect when delivered power drifts from the EMS setpoint. | Regression / Anomaly | Residual model, control charts | EMS, Dispatch | setpoint vs delivered → tracking-error anomaly | Ready
32 | Reliability, O&M & economics | Revenue attribution & what-if | Explain revenue by strategy and simulate counterfactual dispatch. | Regression / Causal | Causal ML, uplift, SHAP | EMS, Dispatch | dispatch, price, energy → revenue drivers | Partial
33 | Reliability, O&M & economics | Availability / downtime prediction | Forecast unavailability to protect market commitments. | Classification | GBM, survival | Alarms, BMS, PCS, HVAC | alarms + telemetry trends → P(downtime) | Partial
34 | Reliability, O&M & economics | Warranty / guarantee monitoring | Track SOH & throughput against contractual degradation curves. | Regression + thresholding | Regression + rules | BMS, Dispatch | SOH, cycles vs guarantee → breach risk | Partial
35 | Reliability, O&M & economics | Digital twin / virtual sensors | Estimate hard-to-measure quantities and simulate plant response. | Surrogate modeling | NN surrogate, Gaussian Process, PINN | BMS, PCS, HVAC, EMS | cheap signals → estimated quantity / plant response | Ready

## By Category
Models by category & feasibility
Category | Models | Ready | Partial | Needs field data
Battery health & safety | 7 | 2 | 2 | 3
Anomaly & fault detection | 6 | 3 | 3 | 0
Forecasting | 5 | 4 | 1 | 0
Optimization & control | 7 | 2 | 5 | 0
Efficiency & performance | 4 | 4 | 0 | 0
Reliability, O&M & economics | 6 | 2 | 3 | 1
TOTAL | 35 | 17 | 14 | 4