## Data
alarm_id | source_system | asset_type | asset_code | alarm_code | alarm_type | severity | severity_level | description | probable_cause | start_time | end_time | duration_min | trigger_value | threshold_value | unit | status | acknowledged_by | acknowledged_at | start_date
BHD-ALM-00001 | BMS | Pack | CONT-S02-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-01 15:50 | 2026-08-01 16:30 | 40 |  |  |  | Cleared |  |  | 2026-08-01
BHD-ALM-00002 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-01 22:10 | 2026-08-01 22:30 | 20 | 31 | 38 | degC | Cleared | j.mehta | 2026-08-01 22:16 | 2026-08-01
BHD-ALM-00003 | BMS | Module | EESL-S02-P03-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-02 02:25 | 2026-08-02 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-08-02 02:31 | 2026-08-02
BHD-ALM-00004 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-02 20:25 | 2026-08-02 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-08-02
BHD-ALM-00005 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-03 02:45 | 2026-08-03 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-08-03 02:49 | 2026-08-03
BHD-ALM-00006 | BMS | Pack | CONT-S02-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-03 15:00 | 2026-08-03 17:00 | 120 |  |  |  | Cleared | j.mehta | 2026-08-03 15:29 | 2026-08-03
BHD-ALM-00007 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-08-03 19:25 | 2026-08-03 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-08-03 19:43 | 2026-08-03
BHD-ALM-00008 | BMS | Pack | CONT-S02-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-04 03:20 | 2026-08-04 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-08-04 03:21 | 2026-08-04
BHD-ALM-00009 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-08-04 07:25 | 2026-08-04 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-08-04
BHD-ALM-00010 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-08-04 17:20 | 2026-08-04 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-08-04 17:24 | 2026-08-04
BHD-ALM-00011 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-05 18:35 | 2026-08-05 19:00 | 25 | 32.358 | 30 | kW | Cleared |  |  | 2026-08-05
BHD-ALM-00012 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-07 06:05 | 2026-08-07 06:20 | 15 | 72.1 | 68 | %RH | Cleared |  |  | 2026-08-07
BHD-ALM-00013 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-07 06:35 | 2026-08-07 07:00 | 25 | 72.6 | 68 | %RH | Cleared |  |  | 2026-08-07
BHD-ALM-00014 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-08-07 18:50 | 2026-08-07 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-08-07 18:57 | 2026-08-07
BHD-ALM-00015 | BMS | Module | EESL-S02-P05-M03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-08 01:10 | 2026-08-08 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-08-08
BHD-ALM-00016 | BMS | System | EESL-BESS-S02 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-08-08 05:30 | 2026-08-08 06:15 | 45 | 1985 | 2100 | kOhm | Cleared | m.rao | 2026-08-08 05:42 | 2026-08-08
BHD-ALM-00017 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-08 05:35 | 2026-08-08 05:50 | 15 | 73.4 | 68 | %RH | Cleared |  |  | 2026-08-08
BHD-ALM-00018 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-08 05:55 | 2026-08-08 06:25 | 30 | 72.5 | 68 | %RH | Cleared |  |  | 2026-08-08
BHD-ALM-00019 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-08 12:15 | 2026-08-08 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-08-08 12:37 | 2026-08-08
BHD-ALM-00020 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-08-08 13:30 | 2026-08-08 13:35 | 5 |  |  |  | Cleared | control-room | 2026-08-08 13:31 | 2026-08-08
BHD-ALM-00021 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-08-09 08:35 | 2026-08-09 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-08-09 08:36 | 2026-08-09
BHD-ALM-00022 | BMS | Module | EESL-S02-P01-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-08-10 15:20 | 2026-08-10 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-08-10 15:29 | 2026-08-10
BHD-ALM-00023 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-10 21:50 | 2026-08-10 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-08-10 21:51 | 2026-08-10
BHD-ALM-00024 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-11 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-08-11 21:11 | 2026-08-11
BHD-ALM-00025 | BMS | Module | EESL-S02-P02-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-12 01:55 | 2026-08-12 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-08-12 01:57 | 2026-08-12
BHD-ALM-00026 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-08-12 14:55 | 2026-08-12 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-08-12 14:56 | 2026-08-12
BHD-ALM-00027 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-13 02:35 | 2026-08-13 03:20 | 45 |  |  |  | Cleared |  |  | 2026-08-13
BHD-ALM-00028 | BMS | Pack | CONT-S02-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-13 18:25 | 2026-08-13 18:35 | 10 |  |  |  | Cleared |  |  | 2026-08-13
BHD-ALM-00029 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-14 03:00 | 2026-08-14 03:15 | 15 | 74.9 | 68 | %RH | Cleared |  |  | 2026-08-14
BHD-ALM-00030 | BMS | Cell | EESL-S02-P01-M01 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-14 03:15 | 2026-08-14 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-08-14 03:17 | 2026-08-14
BHD-ALM-00031 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-14 07:05 | 2026-08-14 07:25 | 20 | 71.4 | 68 | %RH | Cleared |  |  | 2026-08-14
BHD-ALM-00032 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-08-14 10:30 | 2026-08-14 10:40 | 10 |  |  |  | Cleared |  |  | 2026-08-14
BHD-ALM-00033 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-14 19:35 | 2026-08-14 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-08-14
BHD-ALM-00034 | BMS | Cell | EESL-S02-P01-M06 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-15 04:55 | 2026-08-15 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-08-15
BHD-ALM-00035 | BMS | Cell | EESL-S02-P02-M16 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-15 12:55 | 2026-08-15 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-08-15 13:06 | 2026-08-15
BHD-ALM-00036 | BMS | Module | EESL-S02-P03-M08 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-15 17:00 | 2026-08-15 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-08-15
BHD-ALM-00037 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-15 22:15 | 2026-08-15 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-08-15 22:20 | 2026-08-15
BHD-ALM-00038 | BMS | Module | EESL-S02-P03-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-16 00:35 | 2026-08-16 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-08-16 00:41 | 2026-08-16
BHD-ALM-00039 | BMS | Module | EESL-S02-P03-M15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-16 01:25 | 2026-08-16 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-08-16
BHD-ALM-00040 | PCS | Inverter | EESL-BESS-S02-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-08-16 05:10 | 2026-08-16 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-08-16 05:23 | 2026-08-16
BHD-ALM-00041 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-08-16 11:05 | 2026-08-16 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-08-16 11:07 | 2026-08-16
BHD-ALM-00042 | BMS | Module | EESL-S02-P06-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-16 17:35 | 2026-08-16 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-08-16 17:36 | 2026-08-16
BHD-ALM-00043 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-18 08:55 | 2026-08-18 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-08-18
BHD-ALM-00044 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-18 09:35 | 2026-08-18 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-08-18
BHD-ALM-00045 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-08-18 18:40 | 2026-08-18 18:55 | 15 | 1453.005 | 1500 | kVA | Cleared |  |  | 2026-08-18
BHD-ALM-00046 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-19 04:50 | 2026-08-19 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-08-19 04:53 | 2026-08-19
BHD-ALM-00047 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-08-19 12:15 | 2026-08-19 12:40 | 25 |  |  |  | Cleared |  |  | 2026-08-19
BHD-ALM-00048 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-08-19 20:40 | 2026-08-19 21:40 | 60 |  |  |  | Cleared | control-room | 2026-08-19 20:48 | 2026-08-19
BHD-ALM-00049 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-08-20 09:35 | 2026-08-20 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-08-20 09:40 | 2026-08-20
BHD-ALM-00050 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-21 18:10 | 2026-08-21 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-08-21 18:11 | 2026-08-21
BHD-ALM-00051 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-22 05:00 | 2026-08-22 05:15 | 15 | 70.5 | 68 | %RH | Cleared |  |  | 2026-08-22
BHD-ALM-00052 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-22 05:25 | 2026-08-22 05:40 | 15 | 77.3 | 68 | %RH | Cleared |  |  | 2026-08-22
BHD-ALM-00053 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-22 07:50 | 2026-08-22 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-08-22
BHD-ALM-00054 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-23 04:00 | 2026-08-23 05:25 | 85 |  |  |  | Cleared |  |  | 2026-08-23
BHD-ALM-00055 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-23 05:05 | 2026-08-23 05:20 | 15 | 71.6 | 68 | %RH | Cleared |  |  | 2026-08-23
BHD-ALM-00056 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-23 05:40 | 2026-08-23 05:55 | 15 | 74.4 | 68 | %RH | Cleared |  |  | 2026-08-23
BHD-ALM-00057 | BMS | Pack | CONT-S02-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-23 08:30 | 2026-08-23 08:55 | 25 |  |  |  | Cleared |  |  | 2026-08-23
BHD-ALM-00058 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-08-23 22:25 | 2026-08-23 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-08-23 22:26 | 2026-08-23
BHD-ALM-00059 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-24 01:15 | 2026-08-24 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-08-24
BHD-ALM-00060 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-24 12:10 | 2026-08-24 12:25 | 15 |  |  |  | Cleared |  |  | 2026-08-24
BHD-ALM-00061 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-24 21:10 | 2026-08-24 21:35 | 25 | 9.96 | 10 | % | Cleared | control-room | 2026-08-24 21:17 | 2026-08-24
BHD-ALM-00062 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-25 02:50 | 2026-08-25 03:05 | 15 | 30.443 | 30 | kW | Cleared | a.khan | 2026-08-25 02:55 | 2026-08-25
BHD-ALM-00063 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-25 15:10 | 2026-08-25 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-08-25
BHD-ALM-00064 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-25 23:15 | 2026-08-26 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-08-25 23:17 | 2026-08-25
BHD-ALM-00065 | BMS | Module | EESL-S02-P01-M07 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-26 00:55 | 2026-08-26 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-08-26
BHD-ALM-00066 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-26 14:50 | 2026-08-26 15:05 | 15 | 31.794 | 30 | kW | Cleared | a.khan | 2026-08-26 14:53 | 2026-08-26
BHD-ALM-00067 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-26 17:35 | 2026-08-26 17:45 | 10 | 30.513 | 30 | kW | Cleared |  |  | 2026-08-26
BHD-ALM-00068 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-26 20:00 | 2026-08-26 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-08-26
BHD-ALM-00069 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-08-27 01:30 | 2026-08-27 02:05 | 35 | 914.928 | 1500 | kVA | Cleared |  |  | 2026-08-27
BHD-ALM-00070 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-27 09:25 | 2026-08-27 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-08-27 09:58 | 2026-08-27
BHD-ALM-00071 | BMS | Cell | EESL-S02-P06-M03 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-27 13:50 | 2026-08-27 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-08-27 14:13 | 2026-08-27
BHD-ALM-00072 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-27 17:00 | 2026-08-27 17:25 | 25 | 63.51 | 60 | degC | Cleared |  |  | 2026-08-27
BHD-ALM-00073 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-27 17:30 | 2026-08-27 18:10 | 40 | 62.65 | 60 | degC | Cleared |  |  | 2026-08-27
BHD-ALM-00074 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-08-27 22:00 | 2026-08-27 22:05 | 5 |  |  |  | Cleared |  |  | 2026-08-27
BHD-ALM-00075 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-28 08:10 | 2026-08-28 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-08-28
BHD-ALM-00076 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-28 12:25 | 2026-08-28 12:40 | 15 |  |  |  | Cleared |  |  | 2026-08-28
BHD-ALM-00077 | BMS | Module | EESL-S02-P06-M13 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-28 17:05 | 2026-08-28 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-08-28
BHD-ALM-00078 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-28 17:45 | 2026-08-28 18:25 | 40 | 63.81 | 60 | degC | Cleared |  |  | 2026-08-28
BHD-ALM-00079 | BMS | Module | EESL-S02-P01-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-08-28 18:15 | 2026-08-28 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-08-28 18:19 | 2026-08-28
BHD-ALM-00080 | BMS | Module | EESL-S02-P05-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-08-28 18:25 | 2026-08-28 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-08-28 18:43 | 2026-08-28
BHD-ALM-00081 | BMS | Pack | CONT-S02-01-PACK-05 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-29 09:35 | 2026-08-29 09:40 | 5 |  |  |  | Cleared |  |  | 2026-08-29
BHD-ALM-00082 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-29 22:10 | 2026-08-29 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-08-29
BHD-ALM-00083 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-30 02:35 | 2026-08-30 03:20 | 45 |  |  |  | Cleared |  |  | 2026-08-30
BHD-ALM-00084 | BMS | Pack | CONT-S02-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-30 18:25 | 2026-08-30 18:35 | 10 |  |  |  | Cleared |  |  | 2026-08-30
BHD-ALM-00085 | BMS | System | EESL-BESS-S02 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-08-31 22:20 | 2026-08-31 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-08-31 22:32 | 2026-08-31
BHD-ALM-00086 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-01 04:20 | 2026-09-01 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-09-01 04:28 | 2026-09-01
BHD-ALM-00087 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-01 04:50 | 2026-09-01 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-09-01 04:53 | 2026-09-01
BHD-ALM-00088 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-01 12:05 | 2026-09-01 12:35 | 30 |  |  |  | Cleared |  |  | 2026-09-01
BHD-ALM-00089 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-01 12:15 | 2026-09-01 12:40 | 25 |  |  |  | Cleared |  |  | 2026-09-01
BHD-ALM-00090 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-01 17:40 | 2026-09-01 17:50 | 10 | 1395.45 | 1500 | kVA | Cleared |  |  | 2026-09-01
BHD-ALM-00091 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-01 20:40 | 2026-09-01 21:40 | 60 |  |  |  | Cleared | control-room | 2026-09-01 20:48 | 2026-09-01
BHD-ALM-00092 | BMS | Cell | EESL-S02-P06-M01 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-02 03:15 | 2026-09-02 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-09-02 03:17 | 2026-09-02
BHD-ALM-00093 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-02 10:30 | 2026-09-02 10:40 | 10 |  |  |  | Cleared |  |  | 2026-09-02
BHD-ALM-00094 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-02 19:35 | 2026-09-02 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-09-02
BHD-ALM-00095 | BMS | Module | EESL-S02-P04-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-03 15:20 | 2026-09-03 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-09-03 15:29 | 2026-09-03
BHD-ALM-00096 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-03 21:50 | 2026-09-03 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-09-03 21:51 | 2026-09-03
BHD-ALM-00097 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-04 04:40 | 2026-09-04 05:00 | 20 | 70.7 | 68 | %RH | Cleared |  |  | 2026-09-04
BHD-ALM-00098 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-04 05:45 | 2026-09-04 06:05 | 20 | 72.1 | 68 | %RH | Cleared |  |  | 2026-09-04
BHD-ALM-00099 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-04 08:35 | 2026-09-04 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-09-04 08:36 | 2026-09-04
BHD-ALM-00100 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-05 08:55 | 2026-09-05 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-09-05
BHD-ALM-00101 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-05 09:35 | 2026-09-05 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-09-05
BHD-ALM-00102 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-05 18:40 | 2026-09-05 18:55 | 15 | 1453.005 | 1500 | kVA | Cleared |  |  | 2026-09-05
BHD-ALM-00103 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-06 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-09-06 21:11 | 2026-09-06
BHD-ALM-00104 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-07 18:10 | 2026-09-07 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-09-07 18:11 | 2026-09-07
BHD-ALM-00105 | BMS | Module | EESL-S02-P04-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-09 01:55 | 2026-09-09 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-09-09 01:57 | 2026-09-09
BHD-ALM-00106 | BMS | Module | EESL-S02-P06-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-09 13:30 | 2026-09-09 15:45 | 135 | 41.15 | 40 | degC | Cleared | control-room | 2026-09-09 13:42 | 2026-09-09
BHD-ALM-00107 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-09 14:55 | 2026-09-09 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-09-09 14:56 | 2026-09-09
BHD-ALM-00108 | BMS | Module | EESL-S02-P06-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-10 13:10 | 2026-09-10 16:00 | 170 | 41.96 | 40 | degC | Cleared | control-room | 2026-09-10 13:22 | 2026-09-10
BHD-ALM-00109 | BMS | Module | EESL-S02-P06-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-10 17:00 | 2026-09-10 18:05 | 65 | 41.46 | 40 | degC | Cleared | control-room | 2026-09-10 17:12 | 2026-09-10
BHD-ALM-00110 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-10 17:00 | 2026-09-10 17:10 | 10 | 61.25 | 60 | degC | Cleared |  |  | 2026-09-10
BHD-ALM-00111 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-10 17:15 | 2026-09-10 17:30 | 15 | 62.67 | 60 | degC | Cleared |  |  | 2026-09-10
BHD-ALM-00112 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-10 17:35 | 2026-09-10 18:35 | 60 | 63.27 | 60 | degC | Cleared |  |  | 2026-09-10
BHD-ALM-00113 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-10 18:50 | 2026-09-10 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-09-10 18:57 | 2026-09-10
BHD-ALM-00114 | BMS | Cell | EESL-S02-P03-M06 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-11 04:55 | 2026-09-11 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-09-11
BHD-ALM-00115 | BMS | Cell | EESL-S02-P06-M16 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-11 12:55 | 2026-09-11 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-09-11 13:06 | 2026-09-11
BHD-ALM-00116 | BMS | Module | EESL-S02-P01-M08 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-11 17:00 | 2026-09-11 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-09-11
BHD-ALM-00117 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 17:00 | 2026-09-11 17:10 | 10 | 62.06 | 60 | degC | Cleared |  |  | 2026-09-11
BHD-ALM-00118 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 17:35 | 2026-09-11 17:45 | 10 | 63.39 | 60 | degC | Cleared |  |  | 2026-09-11
BHD-ALM-00119 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 17:50 | 2026-09-11 18:20 | 30 | 62.12 | 60 | degC | Cleared |  |  | 2026-09-11
BHD-ALM-00120 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 18:30 | 2026-09-11 18:45 | 15 | 62.43 | 60 | degC | Cleared |  |  | 2026-09-11
BHD-ALM-00121 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-11 22:15 | 2026-09-11 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-09-11 22:20 | 2026-09-11
BHD-ALM-00122 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-12 02:45 | 2026-09-12 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-09-12 02:49 | 2026-09-12
BHD-ALM-00123 | BMS | Pack | CONT-S02-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-12 15:00 | 2026-09-12 17:00 | 120 |  |  |  | Cleared | j.mehta | 2026-09-12 15:29 | 2026-09-12
BHD-ALM-00124 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-09-12 19:25 | 2026-09-12 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-09-12 19:43 | 2026-09-12
BHD-ALM-00125 | BMS | Module | EESL-S02-P06-M07 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-13 00:55 | 2026-09-13 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-09-13
BHD-ALM-00126 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-13 14:50 | 2026-09-13 15:05 | 15 | 31.794 | 30 | kW | Cleared | a.khan | 2026-09-13 14:53 | 2026-09-13
BHD-ALM-00127 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-13 17:35 | 2026-09-13 17:45 | 10 | 30.513 | 30 | kW | Cleared |  |  | 2026-09-13
BHD-ALM-00128 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-13 20:00 | 2026-09-13 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-09-13
BHD-ALM-00129 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-14 18:35 | 2026-09-14 19:00 | 25 | 32.358 | 30 | kW | Cleared |  |  | 2026-09-14
BHD-ALM-00130 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-15 02:50 | 2026-09-15 03:05 | 15 | 30.443 | 30 | kW | Cleared | a.khan | 2026-09-15 02:55 | 2026-09-15
BHD-ALM-00131 | PCS | Inverter | EESL-BESS-S02-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-15 09:00 | 2026-09-15 16:15 | 435 |  |  |  | Cleared | s.iyer | 2026-09-15 09:12 | 2026-09-15
BHD-ALM-00132 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-15 09:05 | 2026-09-15 09:40 | 35 |  |  |  | Cleared | control-room | 2026-09-15 09:17 | 2026-09-15
BHD-ALM-00133 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-15 15:10 | 2026-09-15 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-09-15
BHD-ALM-00134 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-15 23:15 | 2026-09-16 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-09-15 23:17 | 2026-09-15
BHD-ALM-00135 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-16 02:35 | 2026-09-16 03:20 | 45 |  |  |  | Cleared |  |  | 2026-09-16
BHD-ALM-00136 | BMS | Pack | CONT-S02-01-PACK-03 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-16 18:25 | 2026-09-16 18:35 | 10 |  |  |  | Cleared |  |  | 2026-09-16
BHD-ALM-00137 | BMS | Module | EESL-S02-P02-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-17 02:25 | 2026-09-17 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-09-17 02:31 | 2026-09-17
BHD-ALM-00138 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-17 20:25 | 2026-09-17 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-09-17
BHD-ALM-00139 | BMS | Module | EESL-S02-P06-M08 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-18 13:30 | 2026-09-18 16:05 | 155 | 41.23 | 40 | degC | Cleared | control-room | 2026-09-18 13:42 | 2026-09-18
BHD-ALM-00140 | BMS | System | EESL-BESS-S02 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-18 22:20 | 2026-09-18 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-09-18 22:32 | 2026-09-18
BHD-ALM-00141 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-19 09:35 | 2026-09-19 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-09-19 09:40 | 2026-09-19
BHD-ALM-00142 | BMS | Module | EESL-S02-P01-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-20 00:35 | 2026-09-20 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-09-20 00:41 | 2026-09-20
BHD-ALM-00143 | BMS | Module | EESL-S02-P02-M15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-20 01:25 | 2026-09-20 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-09-20
BHD-ALM-00144 | PCS | Inverter | EESL-BESS-S02-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-20 05:10 | 2026-09-20 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-09-20 05:23 | 2026-09-20
BHD-ALM-00145 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-20 11:05 | 2026-09-20 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-09-20 11:07 | 2026-09-20
BHD-ALM-00146 | BMS | Module | EESL-S02-P06-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-20 17:35 | 2026-09-20 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-09-20 17:36 | 2026-09-20
BHD-ALM-00147 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-21 01:15 | 2026-09-21 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-09-21
BHD-ALM-00148 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-21 12:10 | 2026-09-21 12:25 | 15 |  |  |  | Cleared |  |  | 2026-09-21
BHD-ALM-00149 | BMS | System | EESL-BESS-S02 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-21 21:10 | 2026-09-21 21:35 | 25 | 9.96 | 10 | % | Cleared | control-room | 2026-09-21 21:17 | 2026-09-21
BHD-ALM-00150 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-22 04:00 | 2026-09-22 05:25 | 85 |  |  |  | Cleared |  |  | 2026-09-22
BHD-ALM-00151 | BMS | Pack | CONT-S02-01-PACK-02 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-22 08:30 | 2026-09-22 08:55 | 25 |  |  |  | Cleared |  |  | 2026-09-22
BHD-ALM-00152 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-22 22:25 | 2026-09-22 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-09-22 22:26 | 2026-09-22
BHD-ALM-00153 | BMS | Pack | CONT-S02-01-PACK-02 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-23 03:20 | 2026-09-23 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-09-23 03:21 | 2026-09-23
BHD-ALM-00154 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-23 07:25 | 2026-09-23 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-09-23
BHD-ALM-00155 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-23 17:20 | 2026-09-23 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-09-23 17:24 | 2026-09-23
BHD-ALM-00156 | BMS | Module | EESL-S02-P05-M03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-24 01:10 | 2026-09-24 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-09-24
BHD-ALM-00157 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-24 12:15 | 2026-09-24 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-09-24 12:37 | 2026-09-24
BHD-ALM-00158 | BMS | Module | EESL-S02-P06-M13 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-24 13:25 | 2026-09-24 16:15 | 170 | 41.47 | 40 | degC | Cleared | control-room | 2026-09-24 13:37 | 2026-09-24
BHD-ALM-00159 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-24 13:30 | 2026-09-24 13:35 | 5 |  |  |  | Cleared | control-room | 2026-09-24 13:31 | 2026-09-24
BHD-ALM-00160 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-24 17:00 | 2026-09-24 17:10 | 10 | 61.49 | 60 | degC | Cleared |  |  | 2026-09-24
BHD-ALM-00161 | BMS | Module | EESL-S02-P06-M16 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-24 17:05 | 2026-09-24 17:50 | 45 | 40.88 | 40 | degC | Cleared | control-room | 2026-09-24 17:17 | 2026-09-24
BHD-ALM-00162 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-24 17:25 | 2026-09-24 18:20 | 55 | 63.27 | 60 | degC | Cleared |  |  | 2026-09-24
BHD-ALM-00163 | BMS | Module | EESL-S02-P06-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-24 17:55 | 2026-09-24 18:10 | 15 | 40.44 | 40 | degC | Cleared | control-room | 2026-09-24 18:07 | 2026-09-24
BHD-ALM-00164 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-24 18:25 | 2026-09-24 18:45 | 20 | 62.73 | 60 | degC | Cleared |  |  | 2026-09-24
BHD-ALM-00165 | PCS | Inverter | EESL-BESS-S02-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-25 01:30 | 2026-09-25 02:05 | 35 | 914.928 | 1500 | kVA | Cleared |  |  | 2026-09-25
BHD-ALM-00166 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-25 09:25 | 2026-09-25 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-09-25 09:58 | 2026-09-25
BHD-ALM-00167 | BMS | Cell | EESL-S02-P03-M03 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-25 13:50 | 2026-09-25 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-09-25 14:13 | 2026-09-25
BHD-ALM-00168 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-25 17:00 | 2026-09-25 17:25 | 25 | 63.35 | 60 | degC | Cleared |  |  | 2026-09-25
BHD-ALM-00169 | BMS | Module | EESL-S02-P06-M10 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-25 17:05 | 2026-09-25 17:20 | 15 | 40.39 | 40 | degC | Cleared | control-room | 2026-09-25 17:17 | 2026-09-25
BHD-ALM-00170 | BMS | Module | EESL-S02-P06-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-25 17:30 | 2026-09-25 17:45 | 15 | 40.17 | 40 | degC | Cleared | control-room | 2026-09-25 17:42 | 2026-09-25
BHD-ALM-00171 | PCS | Inverter | EESL-BESS-S02-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-25 17:30 | 2026-09-25 18:10 | 40 | 62.51 | 60 | degC | Cleared |  |  | 2026-09-25
BHD-ALM-00172 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-25 22:00 | 2026-09-25 22:05 | 5 |  |  |  | Cleared |  |  | 2026-09-25
BHD-ALM-00173 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-26 08:10 | 2026-09-26 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-26
BHD-ALM-00174 | PCS | Inverter | EESL-BESS-S02-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-26 12:25 | 2026-09-26 12:40 | 15 |  |  |  | Cleared |  |  | 2026-09-26
BHD-ALM-00175 | BMS | Module | EESL-S02-P06-M13 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-26 17:05 | 2026-09-26 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-09-26
BHD-ALM-00176 | BMS | Module | EESL-S02-P04-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-26 18:15 | 2026-09-26 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-09-26 18:19 | 2026-09-26
BHD-ALM-00177 | BMS | Module | EESL-S02-P04-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-26 18:25 | 2026-09-26 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-09-26 18:43 | 2026-09-26
BHD-ALM-00178 | BMS | Module | EESL-S02-P05-M03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-27 01:10 | 2026-09-27 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-09-27
BHD-ALM-00179 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-27 12:15 | 2026-09-27 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-09-27 12:37 | 2026-09-27
BHD-ALM-00180 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-27 13:30 | 2026-09-27 13:35 | 5 |  |  |  | Cleared | control-room | 2026-09-27 13:31 | 2026-09-27
BHD-ALM-00181 | EMS | Site Controller | EESL-BESS-S02-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-28 07:50 | 2026-09-28 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-28
BHD-ALM-00182 | BMS | Pack | CONT-S02-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-29 09:35 | 2026-09-29 09:40 | 5 |  |  |  | Cleared |  |  | 2026-09-29
BHD-ALM-00183 | HVAC | HVAC Unit | EESL-BESS-S02-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-29 22:10 | 2026-09-29 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-09-29