## Data
alarm_id | source_system | asset_type | asset_code | alarm_code | alarm_type | severity | severity_level | description | probable_cause | start_time | end_time | duration_min | trigger_value | threshold_value | unit | status | acknowledged_by | acknowledged_at | start_date
BHU-ALM-00001 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-01 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-09-01 21:11 | 2026-09-01
BHU-ALM-00002 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-02 08:35 | 2026-09-02 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-09-02 08:36 | 2026-09-02
BHU-ALM-00003 | PCS | Inverter | EESL-BESS-S01-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-03 01:30 | 2026-09-03 02:05 | 35 | 1143.66 | 1500 | kVA | Cleared |  |  | 2026-09-03
BHU-ALM-00004 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-03 09:25 | 2026-09-03 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-09-03 09:58 | 2026-09-03
BHU-ALM-00005 | BMS | Cell | EESL-S01-P02-M03 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-03 13:50 | 2026-09-03 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-09-03 14:13 | 2026-09-03
BHU-ALM-00006 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-03 22:00 | 2026-09-03 22:05 | 5 |  |  |  | Cleared |  |  | 2026-09-03
BHU-ALM-00007 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-04 18:35 | 2026-09-04 19:00 | 25 | 32.358 | 30 | kW | Cleared |  |  | 2026-09-04
BHU-ALM-00008 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-05 08:55 | 2026-09-05 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-09-05
BHU-ALM-00009 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-05 09:35 | 2026-09-05 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-09-05
BHU-ALM-00010 | PCS | Inverter | EESL-BESS-S01-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-05 18:40 | 2026-09-05 18:55 | 15 | 1453.005 | 1500 | kVA | Cleared |  |  | 2026-09-05
BHU-ALM-00011 | BMS | Pack | CONT-S01-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-06 09:35 | 2026-09-06 09:40 | 5 |  |  |  | Cleared |  |  | 2026-09-06
BHU-ALM-00012 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-06 22:10 | 2026-09-06 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-09-06
BHU-ALM-00013 | PCS | Inverter | EESL-BESS-S01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-07 18:10 | 2026-09-07 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-09-07 18:11 | 2026-09-07
BHU-ALM-00014 | BMS | Module | EESL-S01-P01-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-08 15:20 | 2026-09-08 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-09-08 15:29 | 2026-09-08
BHU-ALM-00015 | BMS | System | EESL-BESS-S01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-08 21:50 | 2026-09-08 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-09-08 21:51 | 2026-09-08
BHU-ALM-00016 | BMS | Module | EESL-S01-P04-M07 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-09 00:55 | 2026-09-09 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-09-09
BHU-ALM-00017 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-09 14:50 | 2026-09-09 15:05 | 15 | 31.794 | 30 | kW | Cleared | a.khan | 2026-09-09 14:53 | 2026-09-09
BHU-ALM-00018 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-09 17:35 | 2026-09-09 17:45 | 10 | 30.513 | 30 | kW | Cleared |  |  | 2026-09-09
BHU-ALM-00019 | BMS | System | EESL-BESS-S01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-09 20:00 | 2026-09-09 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-09-09
BHU-ALM-00020 | BMS | Cell | EESL-S01-P03-M06 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-10 04:55 | 2026-09-10 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-09-10
BHU-ALM-00021 | BMS | Cell | EESL-S01-P06-M16 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-10 12:55 | 2026-09-10 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-09-10 13:06 | 2026-09-10
BHU-ALM-00022 | BMS | Module | EESL-S01-P06-M08 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-10 17:00 | 2026-09-10 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-09-10
BHU-ALM-00023 | BMS | System | EESL-BESS-S01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-10 22:15 | 2026-09-10 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-09-10 22:20 | 2026-09-10
BHU-ALM-00024 | PCS | Inverter | EESL-BESS-S01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 01:15 | 2026-09-11 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-09-11
BHU-ALM-00025 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-14 08:10 | 2026-09-14 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-14
BHU-ALM-00026 | PCS | Inverter | EESL-BESS-S01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-14 12:25 | 2026-09-14 12:40 | 15 |  |  |  | Cleared |  |  | 2026-09-14
BHU-ALM-00027 | BMS | Module | EESL-S01-P06-M13 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-14 17:05 | 2026-09-14 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-09-14
BHU-ALM-00028 | BMS | Module | EESL-S01-P06-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-14 18:15 | 2026-09-14 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-09-14 18:19 | 2026-09-14
BHU-ALM-00029 | BMS | Module | EESL-S01-P02-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-14 18:25 | 2026-09-14 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-09-14 18:43 | 2026-09-14
BHU-ALM-00030 | PCS | Inverter | EESL-BESS-S01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-15 02:35 | 2026-09-15 03:20 | 45 |  |  |  | Cleared |  |  | 2026-09-15
BHU-ALM-00031 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-15 02:50 | 2026-09-15 03:25 | 35 | 78.4 | 68 | %RH | Cleared |  |  | 2026-09-15
BHU-ALM-00032 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-15 03:30 | 2026-09-15 04:00 | 30 | 75.4 | 68 | %RH | Cleared |  |  | 2026-09-15
BHU-ALM-00033 | BMS | System | EESL-BESS-S01 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-15 05:30 | 2026-09-15 06:15 | 45 | 1985 | 2100 | kOhm | Cleared | m.rao | 2026-09-15 05:42 | 2026-09-15
BHU-ALM-00034 | BMS | Pack | CONT-S01-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-15 18:25 | 2026-09-15 18:35 | 10 |  |  |  | Cleared |  |  | 2026-09-15
BHU-ALM-00035 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-16 07:50 | 2026-09-16 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-16
BHU-ALM-00036 | BMS | Pack | CONT-S01-01-PACK-02 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-17 03:20 | 2026-09-17 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-09-17 03:21 | 2026-09-17
BHU-ALM-00037 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-17 07:25 | 2026-09-17 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-09-17
BHU-ALM-00038 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-17 17:20 | 2026-09-17 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-09-17 17:24 | 2026-09-17
BHU-ALM-00039 | PCS | Inverter | EESL-BESS-S01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-18 04:00 | 2026-09-18 05:25 | 85 |  |  |  | Cleared |  |  | 2026-09-18
BHU-ALM-00040 | BMS | Pack | CONT-S01-01-PACK-04 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-18 08:30 | 2026-09-18 08:55 | 25 |  |  |  | Cleared |  |  | 2026-09-18
BHU-ALM-00041 | PCS | Inverter | EESL-BESS-S01-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-18 22:25 | 2026-09-18 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-09-18 22:26 | 2026-09-18
BHU-ALM-00042 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-19 02:50 | 2026-09-19 03:05 | 15 | 30.443 | 30 | kW | Cleared | a.khan | 2026-09-19 02:55 | 2026-09-19
BHU-ALM-00043 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-19 15:10 | 2026-09-19 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-09-19
BHU-ALM-00044 | BMS | System | EESL-BESS-S01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-19 23:15 | 2026-09-20 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-09-19 23:17 | 2026-09-19
BHU-ALM-00045 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-20 00:15 | 2026-09-20 00:30 | 15 | 79.1 | 68 | %RH | Cleared |  |  | 2026-09-20
BHU-ALM-00046 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-20 03:10 | 2026-09-20 03:30 | 20 | 71.1 | 68 | %RH | Cleared |  |  | 2026-09-20
BHU-ALM-00047 | BMS | System | EESL-BESS-S01 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-20 22:20 | 2026-09-20 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-09-20 22:32 | 2026-09-20
BHU-ALM-00048 | BMS | Cell | EESL-S01-P02-M01 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-21 03:15 | 2026-09-21 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-09-21 03:17 | 2026-09-21
BHU-ALM-00049 | PCS | Inverter | EESL-BESS-S01-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-21 09:00 | 2026-09-21 16:15 | 435 |  |  |  | Cleared | s.iyer | 2026-09-21 09:12 | 2026-09-21
BHU-ALM-00050 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-21 09:05 | 2026-09-21 09:40 | 35 |  |  |  | Cleared | control-room | 2026-09-21 09:17 | 2026-09-21
BHU-ALM-00051 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-21 10:30 | 2026-09-21 10:40 | 10 |  |  |  | Cleared |  |  | 2026-09-21
BHU-ALM-00052 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-21 19:35 | 2026-09-21 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-09-21
BHU-ALM-00053 | BMS | Module | EESL-S01-P02-M03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-22 01:10 | 2026-09-22 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-09-22
BHU-ALM-00054 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-22 12:15 | 2026-09-22 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-09-22 12:37 | 2026-09-22
BHU-ALM-00055 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-22 13:30 | 2026-09-22 13:35 | 5 |  |  |  | Cleared | control-room | 2026-09-22 13:31 | 2026-09-22
BHU-ALM-00056 | BMS | Module | EESL-S01-P03-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-23 02:25 | 2026-09-23 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-09-23 02:31 | 2026-09-23
BHU-ALM-00057 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-23 20:25 | 2026-09-23 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-09-23
BHU-ALM-00058 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-24 18:50 | 2026-09-24 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-09-24 18:57 | 2026-09-24
BHU-ALM-00059 | BMS | Module | EESL-S01-P04-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-25 00:35 | 2026-09-25 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-09-25 00:41 | 2026-09-25
BHU-ALM-00060 | BMS | Module | EESL-S01-P04-M15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-25 01:25 | 2026-09-25 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-09-25
BHU-ALM-00061 | PCS | Inverter | EESL-BESS-S01-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-25 05:10 | 2026-09-25 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-09-25 05:23 | 2026-09-25
BHU-ALM-00062 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-25 11:05 | 2026-09-25 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-09-25 11:07 | 2026-09-25
BHU-ALM-00063 | BMS | Module | EESL-S01-P04-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-25 17:35 | 2026-09-25 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-09-25 17:36 | 2026-09-25
BHU-ALM-00064 | BMS | Module | EESL-S01-P01-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-26 01:55 | 2026-09-26 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-09-26 01:57 | 2026-09-26
BHU-ALM-00065 | BMS | Module | EESL-S01-P06-M08 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-26 13:30 | 2026-09-26 15:45 | 135 | 41.13 | 40 | degC | Cleared | control-room | 2026-09-26 13:42 | 2026-09-26
BHU-ALM-00066 | PCS | Inverter | EESL-BESS-S01-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-26 14:55 | 2026-09-26 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-09-26 14:56 | 2026-09-26
BHU-ALM-00067 | BMS | Module | EESL-S01-P05-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-27 00:35 | 2026-09-27 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-09-27 00:41 | 2026-09-27
BHU-ALM-00068 | BMS | Module | EESL-S01-P04-M15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-27 01:25 | 2026-09-27 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-09-27
BHU-ALM-00069 | PCS | Inverter | EESL-BESS-S01-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-27 05:10 | 2026-09-27 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-09-27 05:23 | 2026-09-27
BHU-ALM-00070 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-27 11:05 | 2026-09-27 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-09-27 11:07 | 2026-09-27
BHU-ALM-00071 | BMS | Module | EESL-S01-P01-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-27 17:35 | 2026-09-27 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-09-27 17:36 | 2026-09-27
BHU-ALM-00072 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-28 09:35 | 2026-09-28 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-09-28 09:40 | 2026-09-28
BHU-ALM-00073 | PCS | Inverter | EESL-BESS-S01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-29 02:45 | 2026-09-29 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-09-29 02:49 | 2026-09-29
BHU-ALM-00074 | BMS | Pack | CONT-S01-01-PACK-04 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-29 15:00 | 2026-09-29 17:00 | 120 |  |  |  | Cleared | j.mehta | 2026-09-29 15:29 | 2026-09-29
BHU-ALM-00075 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-09-29 19:25 | 2026-09-29 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-09-29 19:43 | 2026-09-29
BHU-ALM-00076 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-30 04:20 | 2026-09-30 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-09-30 04:28 | 2026-09-30
BHU-ALM-00077 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-30 04:50 | 2026-09-30 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-09-30 04:53 | 2026-09-30
BHU-ALM-00078 | PCS | Inverter | EESL-BESS-S01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-30 12:05 | 2026-09-30 12:35 | 30 |  |  |  | Cleared |  |  | 2026-09-30
BHU-ALM-00079 | EMS | Site Controller | EESL-BESS-S01-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-30 12:15 | 2026-09-30 12:40 | 25 |  |  |  | Cleared |  |  | 2026-09-30
BHU-ALM-00080 | PCS | Inverter | EESL-BESS-S01-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-30 17:40 | 2026-09-30 17:50 | 10 | 1395.45 | 1500 | kVA | Cleared |  |  | 2026-09-30
BHU-ALM-00081 | HVAC | HVAC Unit | EESL-BESS-S01-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-30 20:40 | 2026-09-30 21:40 | 60 |  |  |  | Cleared | control-room | 2026-09-30 20:48 | 2026-09-30