## Data
alarm_id | source_system | asset_type | asset_code | alarm_code | alarm_type | severity | severity_level | description | probable_cause | start_time | end_time | duration_min | trigger_value | threshold_value | unit | status | acknowledged_by | acknowledged_at | start_date
DHA-ALM-00001 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-01 18:50 | 2026-09-01 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-09-01 18:57 | 2026-09-01
DHA-ALM-00002 | BMS | Cell | EESL-S05-P06-M06 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-02 04:55 | 2026-09-02 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-09-02
DHA-ALM-00003 | BMS | Cell | EESL-S05-P05-M16 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-02 12:55 | 2026-09-02 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-09-02 13:06 | 2026-09-02
DHA-ALM-00004 | BMS | Module | EESL-S05-P04-M08 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-02 17:00 | 2026-09-02 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-09-02
DHA-ALM-00005 | BMS | System | EESL-BESS-S05 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-02 22:15 | 2026-09-02 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-09-02 22:20 | 2026-09-02
DHA-ALM-00006 | BMS | Cell | EESL-S05-P05-M01 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-04 03:15 | 2026-09-04 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-09-04 03:17 | 2026-09-04
DHA-ALM-00007 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-04 10:30 | 2026-09-04 10:40 | 10 |  |  |  | Cleared |  |  | 2026-09-04
DHA-ALM-00008 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-04 19:35 | 2026-09-04 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-09-04
DHA-ALM-00009 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-06 09:35 | 2026-09-06 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-09-06 09:40 | 2026-09-06
DHA-ALM-00010 | BMS | Pack | CONT-S05-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-07 03:20 | 2026-09-07 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-09-07 03:21 | 2026-09-07
DHA-ALM-00011 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-07 07:25 | 2026-09-07 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-09-07
DHA-ALM-00012 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-07 17:20 | 2026-09-07 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-09-07 17:24 | 2026-09-07
DHA-ALM-00013 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-08 04:20 | 2026-09-08 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-09-08 04:28 | 2026-09-08
DHA-ALM-00014 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-08 04:50 | 2026-09-08 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-09-08 04:53 | 2026-09-08
DHA-ALM-00015 | PCS | Inverter | EESL-BESS-S05-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-08 12:05 | 2026-09-08 12:35 | 30 |  |  |  | Cleared |  |  | 2026-09-08
DHA-ALM-00016 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-08 12:15 | 2026-09-08 12:40 | 25 |  |  |  | Cleared |  |  | 2026-09-08
DHA-ALM-00017 | PCS | Inverter | EESL-BESS-S05-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-08 17:40 | 2026-09-08 17:50 | 10 | 1395.45 | 1500 | kVA | Cleared |  |  | 2026-09-08
DHA-ALM-00018 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-08 20:40 | 2026-09-08 21:40 | 60 |  |  |  | Cleared | control-room | 2026-09-08 20:48 | 2026-09-08
DHA-ALM-00019 | BMS | Pack | CONT-S05-01-PACK-02 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-09 09:35 | 2026-09-09 09:40 | 5 |  |  |  | Cleared |  |  | 2026-09-09
DHA-ALM-00020 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-09 22:10 | 2026-09-09 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-09-09
DHA-ALM-00021 | PCS | Inverter | EESL-BESS-S05-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-10 01:30 | 2026-09-10 02:05 | 35 | 1143.66 | 1500 | kVA | Cleared |  |  | 2026-09-10
DHA-ALM-00022 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-10 09:25 | 2026-09-10 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-09-10 09:58 | 2026-09-10
DHA-ALM-00023 | BMS | Cell | EESL-S05-P03-M03 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-10 13:50 | 2026-09-10 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-09-10 14:13 | 2026-09-10
DHA-ALM-00024 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-10 22:00 | 2026-09-10 22:05 | 5 |  |  |  | Cleared |  |  | 2026-09-10
DHA-ALM-00025 | PCS | Inverter | EESL-BESS-S05-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 01:15 | 2026-09-11 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-09-11
DHA-ALM-00026 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-12 04:20 | 2026-09-12 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-09-12 04:28 | 2026-09-12
DHA-ALM-00027 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-12 04:50 | 2026-09-12 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-09-12 04:53 | 2026-09-12
DHA-ALM-00028 | PCS | Inverter | EESL-BESS-S05-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-12 12:05 | 2026-09-12 12:35 | 30 |  |  |  | Cleared |  |  | 2026-09-12
DHA-ALM-00029 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-12 12:15 | 2026-09-12 12:40 | 25 |  |  |  | Cleared |  |  | 2026-09-12
DHA-ALM-00030 | PCS | Inverter | EESL-BESS-S05-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-12 17:40 | 2026-09-12 17:50 | 10 | 1395.45 | 1500 | kVA | Cleared |  |  | 2026-09-12
DHA-ALM-00031 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-12 20:40 | 2026-09-12 21:40 | 60 |  |  |  | Cleared | control-room | 2026-09-12 20:48 | 2026-09-12
DHA-ALM-00032 | BMS | Module | EESL-S05-P06-M07 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-13 00:55 | 2026-09-13 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-09-13
DHA-ALM-00033 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-13 14:50 | 2026-09-13 15:05 | 15 | 31.794 | 30 | kW | Cleared | a.khan | 2026-09-13 14:53 | 2026-09-13
DHA-ALM-00034 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-13 17:35 | 2026-09-13 17:45 | 10 | 30.513 | 30 | kW | Cleared |  |  | 2026-09-13
DHA-ALM-00035 | BMS | System | EESL-BESS-S05 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-13 20:00 | 2026-09-13 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-09-13
DHA-ALM-00036 | BMS | Module | EESL-S05-P05-M03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-14 01:10 | 2026-09-14 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-09-14
DHA-ALM-00037 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-14 12:15 | 2026-09-14 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-09-14 12:37 | 2026-09-14
DHA-ALM-00038 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-14 13:30 | 2026-09-14 13:35 | 5 |  |  |  | Cleared | control-room | 2026-09-14 13:31 | 2026-09-14
DHA-ALM-00039 | PCS | Inverter | EESL-BESS-S05-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-15 02:45 | 2026-09-15 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-09-15 02:49 | 2026-09-15
DHA-ALM-00040 | BMS | Pack | CONT-S05-01-PACK-05 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-15 15:00 | 2026-09-15 17:00 | 120 |  |  |  | Cleared | j.mehta | 2026-09-15 15:29 | 2026-09-15
DHA-ALM-00041 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-09-15 19:25 | 2026-09-15 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-09-15 19:43 | 2026-09-15
DHA-ALM-00042 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-16 03:00 | 2026-09-16 03:20 | 20 | 72.4 | 68 | %RH | Cleared |  |  | 2026-09-16
DHA-ALM-00043 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-16 03:30 | 2026-09-16 04:10 | 40 | 74.4 | 68 | %RH | Cleared |  |  | 2026-09-16
DHA-ALM-00044 | BMS | System | EESL-BESS-S05 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-16 05:30 | 2026-09-16 06:15 | 45 | 1985 | 2100 | kOhm | Cleared | m.rao | 2026-09-16 05:42 | 2026-09-16
DHA-ALM-00045 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-16 08:10 | 2026-09-16 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-16
DHA-ALM-00046 | PCS | Inverter | EESL-BESS-S05-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-16 12:25 | 2026-09-16 12:40 | 15 |  |  |  | Cleared |  |  | 2026-09-16
DHA-ALM-00047 | BMS | Module | EESL-S05-P01-M13 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-16 17:05 | 2026-09-16 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-09-16
DHA-ALM-00048 | BMS | Module | EESL-S05-P03-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-16 18:15 | 2026-09-16 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-09-16 18:19 | 2026-09-16
DHA-ALM-00049 | BMS | Module | EESL-S05-P03-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-16 18:25 | 2026-09-16 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-09-16 18:43 | 2026-09-16
DHA-ALM-00050 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-17 07:50 | 2026-09-17 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-17
DHA-ALM-00051 | BMS | Module | EESL-S05-P02-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-18 02:25 | 2026-09-18 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-09-18 02:31 | 2026-09-18
DHA-ALM-00052 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-18 20:25 | 2026-09-18 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-09-18
DHA-ALM-00053 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-19 03:50 | 2026-09-19 04:10 | 20 | 70.8 | 68 | %RH | Cleared |  |  | 2026-09-19
DHA-ALM-00054 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-19 05:15 | 2026-09-19 05:30 | 15 | 76.4 | 68 | %RH | Cleared |  |  | 2026-09-19
DHA-ALM-00055 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-19 08:55 | 2026-09-19 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-09-19
DHA-ALM-00056 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-19 09:35 | 2026-09-19 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-09-19
DHA-ALM-00057 | PCS | Inverter | EESL-BESS-S05-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-19 18:40 | 2026-09-19 18:55 | 15 | 508.552 | 1500 | kVA | Cleared |  |  | 2026-09-19
DHA-ALM-00058 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-20 02:50 | 2026-09-20 03:05 | 15 | 10.655 | 30 | kW | Cleared | a.khan | 2026-09-20 02:55 | 2026-09-20
DHA-ALM-00059 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-20 03:25 | 2026-09-20 03:45 | 20 | 75.5 | 68 | %RH | Cleared |  |  | 2026-09-20
DHA-ALM-00060 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-20 03:55 | 2026-09-20 04:20 | 25 | 73.8 | 68 | %RH | Cleared |  |  | 2026-09-20
DHA-ALM-00061 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-20 15:10 | 2026-09-20 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-09-20
DHA-ALM-00062 | BMS | System | EESL-BESS-S05 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-20 23:15 | 2026-09-21 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-09-20 23:17 | 2026-09-20
DHA-ALM-00063 | PCS | Inverter | EESL-BESS-S05-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-21 09:00 | 2026-09-21 16:15 | 435 |  |  |  | Cleared | s.iyer | 2026-09-21 09:12 | 2026-09-21
DHA-ALM-00064 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-21 09:05 | 2026-09-21 09:40 | 35 |  |  |  | Cleared | control-room | 2026-09-21 09:17 | 2026-09-21
DHA-ALM-00065 | BMS | System | EESL-BESS-S05 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-21 22:20 | 2026-09-21 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-09-21 22:32 | 2026-09-21
DHA-ALM-00066 | BMS | Module | EESL-S05-P02-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-22 15:20 | 2026-09-22 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-09-22 15:29 | 2026-09-22
DHA-ALM-00067 | BMS | System | EESL-BESS-S05 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-22 21:50 | 2026-09-22 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-09-22 21:51 | 2026-09-22
DHA-ALM-00068 | PCS | Inverter | EESL-BESS-S05-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-23 18:10 | 2026-09-23 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-09-23 18:11 | 2026-09-23
DHA-ALM-00069 | BMS | Module | EESL-S05-P03-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-24 00:35 | 2026-09-24 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-09-24 00:41 | 2026-09-24
DHA-ALM-00070 | BMS | Module | EESL-S05-P05-M15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-24 01:25 | 2026-09-24 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-09-24
DHA-ALM-00071 | PCS | Inverter | EESL-BESS-S05-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-24 05:10 | 2026-09-24 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-09-24 05:23 | 2026-09-24
DHA-ALM-00072 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-24 11:05 | 2026-09-24 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-09-24 11:07 | 2026-09-24
DHA-ALM-00073 | BMS | Module | EESL-S05-P03-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-24 17:35 | 2026-09-24 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-09-24 17:36 | 2026-09-24
DHA-ALM-00074 | BMS | Module | EESL-S05-P03-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-25 01:55 | 2026-09-25 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-09-25 01:57 | 2026-09-25
DHA-ALM-00075 | PCS | Inverter | EESL-BESS-S05-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-25 14:55 | 2026-09-25 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-09-25 14:56 | 2026-09-25
DHA-ALM-00076 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-26 | 2026-09-26 00:15 | 15 | 74.4 | 68 | %RH | Cleared |  |  | 2026-09-26
DHA-ALM-00077 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-26 03:25 | 2026-09-26 04:05 | 40 | 77.7 | 68 | %RH | Cleared |  |  | 2026-09-26
DHA-ALM-00078 | EMS | Site Controller | EESL-BESS-S05-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-26 18:35 | 2026-09-26 19:00 | 25 | 11.325 | 30 | kW | Cleared |  |  | 2026-09-26
DHA-ALM-00079 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-27 03:25 | 2026-09-27 03:40 | 15 | 70.9 | 68 | %RH | Cleared |  |  | 2026-09-27
DHA-ALM-00080 | PCS | Inverter | EESL-BESS-S05-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-27 04:00 | 2026-09-27 05:25 | 85 |  |  |  | Cleared |  |  | 2026-09-27
DHA-ALM-00081 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-27 04:40 | 2026-09-27 05:00 | 20 | 72.6 | 68 | %RH | Cleared |  |  | 2026-09-27
DHA-ALM-00082 | BMS | Pack | CONT-S05-01-PACK-05 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-27 08:30 | 2026-09-27 08:55 | 25 |  |  |  | Cleared |  |  | 2026-09-27
DHA-ALM-00083 | PCS | Inverter | EESL-BESS-S05-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-27 22:25 | 2026-09-27 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-09-27 22:26 | 2026-09-27
DHA-ALM-00084 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-28 03:15 | 2026-09-28 03:40 | 25 | 77.8 | 68 | %RH | Cleared |  |  | 2026-09-28
DHA-ALM-00085 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-28 05:35 | 2026-09-28 06:15 | 40 | 78.9 | 68 | %RH | Cleared |  |  | 2026-09-28
DHA-ALM-00086 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-28 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-09-28 21:11 | 2026-09-28
DHA-ALM-00087 | PCS | Inverter | EESL-BESS-S05-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-29 02:35 | 2026-09-29 03:20 | 45 |  |  |  | Cleared |  |  | 2026-09-29
DHA-ALM-00088 | BMS | Pack | CONT-S05-01-PACK-06 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-29 18:25 | 2026-09-29 18:35 | 10 |  |  |  | Cleared |  |  | 2026-09-29
DHA-ALM-00089 | HVAC | HVAC Unit | EESL-BESS-S05-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-30 08:35 | 2026-09-30 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-09-30 08:36 | 2026-09-30