## Data
alarm_id | source_system | asset_type | asset_code | alarm_code | alarm_type | severity | severity_level | description | probable_cause | start_time | end_time | duration_min | trigger_value | threshold_value | unit | status | acknowledged_by | acknowledged_at | start_date
KOL-ALM-00001 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-01 18:35 | 2026-09-01 19:00 | 25 | 215.72 | 200 | kW | Cleared |  |  | 2026-09-01
KOL-ALM-00002 | BMS | Pack | 01-01-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-02 09:35 | 2026-09-02 09:40 | 5 |  |  |  | Cleared |  |  | 2026-09-02
KOL-ALM-00003 | PCS | Inverter | 01-01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-02 17:10 | 2026-09-02 17:25 | 15 | 60.45 | 60 | degC | Cleared |  |  | 2026-09-02
KOL-ALM-00004 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-02 22:10 | 2026-09-02 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-09-02
KOL-ALM-00005 | BMS | Cell | 01-01-01-01-MODULE-14 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-03 04:55 | 2026-09-03 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-09-03
KOL-ALM-00006 | BMS | Cell | 01-01-01-01-MODULE-9 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-03 12:55 | 2026-09-03 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-09-03 13:06 | 2026-09-03
KOL-ALM-00007 | BMS | Module | 01-01-01-01-MODULE-16 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-03 17:00 | 2026-09-03 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-09-03
KOL-ALM-00008 | PCS | Inverter | 01-01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-03 17:50 | 2026-09-03 18:00 | 10 | 60.39 | 60 | degC | Cleared |  |  | 2026-09-03
KOL-ALM-00009 | BMS | System | 01-BATTERY-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-03 22:15 | 2026-09-03 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-09-03 22:20 | 2026-09-03
KOL-ALM-00010 | BMS | Module | 01-01-01-01-MODULE-15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-04 00:55 | 2026-09-04 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-09-04
KOL-ALM-00011 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-04 14:50 | 2026-09-04 15:05 | 15 | 211.96 | 200 | kW | Cleared | a.khan | 2026-09-04 14:53 | 2026-09-04
KOL-ALM-00012 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-04 17:35 | 2026-09-04 17:45 | 10 | 203.42 | 200 | kW | Cleared |  |  | 2026-09-04
KOL-ALM-00013 | BMS | System | 01-BATTERY-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-04 20:00 | 2026-09-04 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-09-04
KOL-ALM-00014 | PCS | Inverter | 01-01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-05 02:35 | 2026-09-05 03:20 | 45 |  |  |  | Cleared |  |  | 2026-09-05
KOL-ALM-00015 | BMS | Pack | 01-01-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-05 18:25 | 2026-09-05 18:35 | 10 |  |  |  | Cleared |  |  | 2026-09-05
KOL-ALM-00016 | BMS | Cell | 01-01-01-01-MODULE-1 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-06 03:15 | 2026-09-06 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-09-06 03:17 | 2026-09-06
KOL-ALM-00017 | EMS | Site Controller | EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-06 10:30 | 2026-09-06 10:40 | 10 |  |  |  | Cleared |  |  | 2026-09-06
KOL-ALM-00018 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-06 19:35 | 2026-09-06 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-09-06
KOL-ALM-00019 | HVAC | HVAC Unit | HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-08 08:35 | 2026-09-08 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-09-08 08:36 | 2026-09-08
KOL-ALM-00020 | PCS | Inverter | 01-01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-09 01:15 | 2026-09-09 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-09-09
KOL-ALM-00021 | PCS | Inverter | 01-01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-09 12:10 | 2026-09-09 12:25 | 15 |  |  |  | Cleared |  |  | 2026-09-09
KOL-ALM-00022 | BMS | System | 01-BATTERY-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-09 21:10 | 2026-09-09 21:35 | 25 | 9.96 | 10 | % | Cleared | control-room | 2026-09-09 21:17 | 2026-09-09
KOL-ALM-00023 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-10 02:50 | 2026-09-10 03:05 | 15 | 202.95 | 200 | kW | Cleared | a.khan | 2026-09-10 02:55 | 2026-09-10
KOL-ALM-00024 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-10 15:10 | 2026-09-10 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-09-10
KOL-ALM-00025 | BMS | System | 01-BATTERY-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-10 23:15 | 2026-09-11 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-09-10 23:17 | 2026-09-10
KOL-ALM-00026 | PCS | Inverter | 01-01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 02:45 | 2026-09-11 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-09-11 02:49 | 2026-09-11
KOL-ALM-00027 | HVAC | HVAC Unit | HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-09-11 19:25 | 2026-09-11 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-09-11 19:43 | 2026-09-11
KOL-ALM-00028 | EMS | Site Controller | EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-12 09:35 | 2026-09-12 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-09-12 09:40 | 2026-09-12
KOL-ALM-00029 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-13 07:50 | 2026-09-13 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-13
KOL-ALM-00030 | BMS | Module | 01-01-01-01-MODULE-11 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-14 01:10 | 2026-09-14 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-09-14
KOL-ALM-00031 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-14 12:15 | 2026-09-14 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-09-14 12:37 | 2026-09-14
KOL-ALM-00032 | HVAC | HVAC Unit | HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-14 13:30 | 2026-09-14 13:35 | 5 |  |  |  | Cleared | control-room | 2026-09-14 13:31 | 2026-09-14
KOL-ALM-00033 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-15 03:35 | 2026-09-15 03:50 | 15 | 70 | 68 | %RH | Cleared |  |  | 2026-09-15
KOL-ALM-00034 | BMS | System | 01-BATTERY-01 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-15 05:30 | 2026-09-15 06:15 | 45 | 1985 | 2100 | kOhm | Cleared | m.rao | 2026-09-15 05:42 | 2026-09-15
KOL-ALM-00035 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-15 06:00 | 2026-09-15 06:15 | 15 | 69.7 | 68 | %RH | Cleared |  |  | 2026-09-15
KOL-ALM-00036 | BMS | System | 01-BATTERY-01 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-15 22:20 | 2026-09-15 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-09-15 22:32 | 2026-09-15
KOL-ALM-00037 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-16 | 2026-09-16 00:25 | 25 | 70.7 | 68 | %RH | Cleared |  |  | 2026-09-16
KOL-ALM-00038 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-16 03:55 | 2026-09-16 04:15 | 20 | 70.6 | 68 | %RH | Cleared |  |  | 2026-09-16
KOL-ALM-00039 | BMS | Module | 01-01-01-01-MODULE-14 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-17 01:55 | 2026-09-17 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-09-17 01:57 | 2026-09-17
KOL-ALM-00040 | PCS | Inverter | 01-01-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-17 14:55 | 2026-09-17 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-09-17 14:56 | 2026-09-17
KOL-ALM-00041 | BMS | Module | 01-01-01-01-MODULE-2 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-18 00:35 | 2026-09-18 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-09-18 00:41 | 2026-09-18
KOL-ALM-00042 | BMS | Module | 01-01-01-01-MODULE-8 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-18 01:25 | 2026-09-18 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-09-18
KOL-ALM-00043 | PCS | Inverter | 01-01-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-18 05:10 | 2026-09-18 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-09-18 05:23 | 2026-09-18
KOL-ALM-00044 | EMS | Site Controller | EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-18 11:05 | 2026-09-18 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-09-18 11:07 | 2026-09-18
KOL-ALM-00045 | BMS | Module | 01-01-01-01-MODULE-2 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-18 17:35 | 2026-09-18 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-09-18 17:36 | 2026-09-18
KOL-ALM-00046 | BMS | Module | 01-01-01-01-MODULE-12 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-19 15:20 | 2026-09-19 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-09-19 15:29 | 2026-09-19
KOL-ALM-00047 | BMS | System | 01-BATTERY-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-19 21:50 | 2026-09-19 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-09-19 21:51 | 2026-09-19
KOL-ALM-00048 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-20 08:55 | 2026-09-20 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-09-20
KOL-ALM-00049 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-20 09:35 | 2026-09-20 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-09-20
KOL-ALM-00050 | PCS | Inverter | 01-01-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-20 18:40 | 2026-09-20 18:55 | 15 | 9686.7 | 10000 | kVA | Cleared |  |  | 2026-09-20
KOL-ALM-00051 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-21 08:10 | 2026-09-21 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-21
KOL-ALM-00052 | PCS | Inverter | 01-01-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-21 09:00 | 2026-09-21 16:15 | 435 |  |  |  | Cleared | s.iyer | 2026-09-21 09:12 | 2026-09-21
KOL-ALM-00053 | EMS | Site Controller | EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-21 09:05 | 2026-09-21 09:40 | 35 |  |  |  | Cleared | control-room | 2026-09-21 09:17 | 2026-09-21
KOL-ALM-00054 | BMS | Module | 01-01-01-01-MODULE-6 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-21 17:05 | 2026-09-21 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-09-21
KOL-ALM-00055 | BMS | Module | 01-01-01-01-MODULE-12 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-21 18:15 | 2026-09-21 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-09-21 18:19 | 2026-09-21
KOL-ALM-00056 | BMS | Module | 01-01-01-01-MODULE-2 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-21 18:25 | 2026-09-21 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-09-21 18:43 | 2026-09-21
KOL-ALM-00057 | EMS | Site Controller | EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-22 18:50 | 2026-09-22 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-09-22 18:57 | 2026-09-22
KOL-ALM-00058 | PCS | Inverter | 01-01-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-23 01:30 | 2026-09-23 02:05 | 35 | 7624.4 | 10000 | kVA | Cleared |  |  | 2026-09-23
KOL-ALM-00059 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-23 09:25 | 2026-09-23 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-09-23 09:58 | 2026-09-23
KOL-ALM-00060 | BMS | Cell | 01-01-01-01-MODULE-11 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-23 13:50 | 2026-09-23 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-09-23 14:13 | 2026-09-23
KOL-ALM-00061 | EMS | Site Controller | EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-23 22:00 | 2026-09-23 22:05 | 5 |  |  |  | Cleared |  |  | 2026-09-23
KOL-ALM-00062 | PCS | Inverter | 01-01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-24 04:00 | 2026-09-24 05:25 | 85 |  |  |  | Cleared |  |  | 2026-09-24
KOL-ALM-00063 | BMS | Pack | 01-01-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-24 08:30 | 2026-09-24 08:55 | 25 |  |  |  | Cleared |  |  | 2026-09-24
KOL-ALM-00064 | PCS | Inverter | 01-01-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-24 22:25 | 2026-09-24 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-09-24 22:26 | 2026-09-24
KOL-ALM-00065 | EMS | Site Controller | EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-25 04:20 | 2026-09-25 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-09-25 04:28 | 2026-09-25
KOL-ALM-00066 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-25 04:50 | 2026-09-25 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-09-25 04:53 | 2026-09-25
KOL-ALM-00067 | PCS | Inverter | 01-01-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-25 12:05 | 2026-09-25 12:35 | 30 |  |  |  | Cleared |  |  | 2026-09-25
KOL-ALM-00068 | EMS | Site Controller | EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-25 12:15 | 2026-09-25 12:40 | 25 |  |  |  | Cleared |  |  | 2026-09-25
KOL-ALM-00069 | PCS | Inverter | 01-01-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-25 17:40 | 2026-09-25 17:50 | 10 | 9303 | 10000 | kVA | Cleared |  |  | 2026-09-25
KOL-ALM-00070 | HVAC | HVAC Unit | HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-25 20:40 | 2026-09-25 21:40 | 60 |  |  |  | Cleared | control-room | 2026-09-25 20:48 | 2026-09-25
KOL-ALM-00071 | PCS | Inverter | 01-01-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-26 18:10 | 2026-09-26 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-09-26 18:11 | 2026-09-26
KOL-ALM-00072 | BMS | Pack | 01-01-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-27 03:20 | 2026-09-27 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-09-27 03:21 | 2026-09-27
KOL-ALM-00073 | HVAC | HVAC Unit | HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-27 07:25 | 2026-09-27 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-09-27
KOL-ALM-00074 | HVAC | HVAC Unit | HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-27 17:20 | 2026-09-27 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-09-27 17:24 | 2026-09-27
KOL-ALM-00075 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-28 03:25 | 2026-09-28 03:40 | 15 | 73.7 | 68 | %RH | Cleared |  |  | 2026-09-28
KOL-ALM-00076 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-28 05:55 | 2026-09-28 06:15 | 20 | 76.9 | 68 | %RH | Cleared |  |  | 2026-09-28
KOL-ALM-00077 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-28 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-09-28 21:11 | 2026-09-28
KOL-ALM-00078 | BMS | Module | 01-01-01-01-MODULE-14 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-29 02:25 | 2026-09-29 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-09-29 02:31 | 2026-09-29
KOL-ALM-00079 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-29 20:25 | 2026-09-29 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-09-29
KOL-ALM-00080 | BMS | Module | 01-01-01-01-MODULE-14 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-30 02:25 | 2026-09-30 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-09-30 02:31 | 2026-09-30
KOL-ALM-00081 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-30 20:25 | 2026-09-30 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-09-30