## Data
alarm_id | source_system | asset_type | asset_code | alarm_code | alarm_type | severity | severity_level | description | probable_cause | start_time | end_time | duration_min | trigger_value | threshold_value | unit | status | acknowledged_by | acknowledged_at | start_date
PAV-ALM-00001 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-01 08:10 | 2026-09-01 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-01
PAV-ALM-00002 | PCS | Inverter | EESL-BESS-S03-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-01 12:25 | 2026-09-01 12:40 | 15 |  |  |  | Cleared |  |  | 2026-09-01
PAV-ALM-00003 | BMS | Module | EESL-S03-P06-M13 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-01 17:05 | 2026-09-01 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-09-01
PAV-ALM-00004 | BMS | Module | EESL-S03-P06-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-01 18:15 | 2026-09-01 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-09-01 18:19 | 2026-09-01
PAV-ALM-00005 | BMS | Module | EESL-S03-P03-M09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-01 18:25 | 2026-09-01 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-09-01 18:43 | 2026-09-01
PAV-ALM-00006 | BMS | System | EESL-BESS-S03 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-02 22:20 | 2026-09-02 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-09-02 22:32 | 2026-09-02
PAV-ALM-00007 | BMS | Module | EESL-S03-P03-M04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-09-03 15:20 | 2026-09-03 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-09-03 15:29 | 2026-09-03
PAV-ALM-00008 | BMS | System | EESL-BESS-S03 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-03 21:50 | 2026-09-03 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-09-03 21:51 | 2026-09-03
PAV-ALM-00009 | PCS | Inverter | EESL-BESS-S03-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-04 04:00 | 2026-09-04 05:25 | 85 |  |  |  | Cleared |  |  | 2026-09-04
PAV-ALM-00010 | BMS | Pack | CONT-S03-01-PACK-05 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-04 08:30 | 2026-09-04 08:55 | 25 |  |  |  | Cleared |  |  | 2026-09-04
PAV-ALM-00011 | PCS | Inverter | EESL-BESS-S03-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-04 22:25 | 2026-09-04 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-09-04 22:26 | 2026-09-04
PAV-ALM-00012 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-05 07:50 | 2026-09-05 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-09-05
PAV-ALM-00013 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-06 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-09-06 21:11 | 2026-09-06
PAV-ALM-00014 | BMS | Module | EESL-S03-P03-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-07 02:25 | 2026-09-07 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-09-07 02:31 | 2026-09-07
PAV-ALM-00015 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-07 20:25 | 2026-09-07 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-09-07
PAV-ALM-00016 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-08 18:50 | 2026-09-08 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-09-08 18:57 | 2026-09-08
PAV-ALM-00017 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-09 18:35 | 2026-09-09 19:00 | 25 | 32.358 | 30 | kW | Cleared |  |  | 2026-09-09
PAV-ALM-00018 | PCS | Inverter | EESL-BESS-S03-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-10 01:15 | 2026-09-10 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-09-10
PAV-ALM-00019 | PCS | Inverter | EESL-BESS-S03-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-10 12:10 | 2026-09-10 12:25 | 15 |  |  |  | Cleared |  |  | 2026-09-10
PAV-ALM-00020 | BMS | System | EESL-BESS-S03 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-10 21:10 | 2026-09-10 21:35 | 25 | 9.96 | 10 | % | Cleared | control-room | 2026-09-10 21:17 | 2026-09-10
PAV-ALM-00021 | PCS | Inverter | EESL-BESS-S03-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-11 02:45 | 2026-09-11 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-09-11 02:49 | 2026-09-11
PAV-ALM-00022 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-09-11 19:25 | 2026-09-11 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-09-11 19:43 | 2026-09-11
PAV-ALM-00023 | PCS | Inverter | EESL-BESS-S03-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-12 02:35 | 2026-09-12 03:20 | 45 |  |  |  | Cleared |  |  | 2026-09-12
PAV-ALM-00024 | BMS | System | EESL-BESS-S03 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-09-12 05:30 | 2026-09-12 06:15 | 45 | 1985 | 2100 | kOhm | Cleared | m.rao | 2026-09-12 05:42 | 2026-09-12
PAV-ALM-00025 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-12 05:40 | 2026-09-12 05:55 | 15 | 73.6 | 68 | %RH | Cleared |  |  | 2026-09-12
PAV-ALM-00026 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-12 07:35 | 2026-09-12 07:50 | 15 | 72.7 | 68 | %RH | Cleared |  |  | 2026-09-12
PAV-ALM-00027 | BMS | Pack | CONT-S03-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-12 18:25 | 2026-09-12 18:35 | 10 |  |  |  | Cleared |  |  | 2026-09-12
PAV-ALM-00028 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-13 04:40 | 2026-09-13 05:00 | 20 | 70.7 | 68 | %RH | Cleared |  |  | 2026-09-13
PAV-ALM-00029 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-13 05:45 | 2026-09-13 06:05 | 20 | 72.1 | 68 | %RH | Cleared |  |  | 2026-09-13
PAV-ALM-00030 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-13 08:35 | 2026-09-13 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-09-13 08:36 | 2026-09-13
PAV-ALM-00031 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-14 02:50 | 2026-09-14 03:05 | 15 | 30.443 | 30 | kW | Cleared | a.khan | 2026-09-14 02:55 | 2026-09-14
PAV-ALM-00032 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-14 15:10 | 2026-09-14 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-09-14
PAV-ALM-00033 | BMS | System | EESL-BESS-S03 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-14 23:15 | 2026-09-15 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-09-14 23:17 | 2026-09-14
PAV-ALM-00034 | BMS | Module | EESL-S03-P06-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-15 00:35 | 2026-09-15 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-09-15 00:41 | 2026-09-15
PAV-ALM-00035 | BMS | Module | EESL-S03-P05-M15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-15 01:25 | 2026-09-15 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-09-15
PAV-ALM-00036 | PCS | Inverter | EESL-BESS-S03-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-15 05:10 | 2026-09-15 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-09-15 05:23 | 2026-09-15
PAV-ALM-00037 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-15 11:05 | 2026-09-15 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-09-15 11:07 | 2026-09-15
PAV-ALM-00038 | BMS | Module | EESL-S03-P05-M09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-15 17:35 | 2026-09-15 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-09-15 17:36 | 2026-09-15
PAV-ALM-00039 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-09-16 09:35 | 2026-09-16 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-09-16 09:40 | 2026-09-16
PAV-ALM-00040 | BMS | Cell | EESL-S03-P05-M06 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-17 04:55 | 2026-09-17 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-09-17
PAV-ALM-00041 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-17 10:25 | 2026-09-17 10:40 | 15 | 74.7 | 68 | %RH | Cleared |  |  | 2026-09-17
PAV-ALM-00042 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-17 12:05 | 2026-09-17 12:30 | 25 | 74.3 | 68 | %RH | Cleared |  |  | 2026-09-17
PAV-ALM-00043 | BMS | Cell | EESL-S03-P01-M16 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-17 12:55 | 2026-09-17 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-09-17 13:06 | 2026-09-17
PAV-ALM-00044 | BMS | Module | EESL-S03-P02-M08 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-17 17:00 | 2026-09-17 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-09-17
PAV-ALM-00045 | BMS | System | EESL-BESS-S03 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-17 22:15 | 2026-09-17 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-09-17 22:20 | 2026-09-17
PAV-ALM-00046 | BMS | Pack | CONT-S03-01-PACK-04 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-18 09:35 | 2026-09-18 09:40 | 5 |  |  |  | Cleared |  |  | 2026-09-18
PAV-ALM-00047 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-18 22:10 | 2026-09-18 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-09-18
PAV-ALM-00048 | PCS | Inverter | EESL-BESS-S03-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-19 01:30 | 2026-09-19 02:05 | 35 | 914.928 | 1500 | kVA | Cleared |  |  | 2026-09-19
PAV-ALM-00049 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-19 09:25 | 2026-09-19 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-09-19 09:58 | 2026-09-19
PAV-ALM-00050 | BMS | Cell | EESL-S03-P06-M03 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-19 13:50 | 2026-09-19 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-09-19 14:13 | 2026-09-19
PAV-ALM-00051 | PCS | Inverter | EESL-BESS-S03-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-19 17:10 | 2026-09-19 17:25 | 15 | 61.46 | 60 | degC | Cleared |  |  | 2026-09-19
PAV-ALM-00052 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-19 22:00 | 2026-09-19 22:05 | 5 |  |  |  | Cleared |  |  | 2026-09-19
PAV-ALM-00053 | PCS | Inverter | EESL-BESS-S03-PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-09-21 09:00 | 2026-09-21 16:15 | 435 |  |  |  | Cleared | s.iyer | 2026-09-21 09:12 | 2026-09-21
PAV-ALM-00054 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-21 09:05 | 2026-09-21 09:40 | 35 |  |  |  | Cleared | control-room | 2026-09-21 09:17 | 2026-09-21
PAV-ALM-00055 | BMS | Pack | CONT-S03-01-PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-22 03:20 | 2026-09-22 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-09-22 03:21 | 2026-09-22
PAV-ALM-00056 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-22 07:25 | 2026-09-22 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-09-22
PAV-ALM-00057 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-09-22 17:20 | 2026-09-22 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-09-22 17:24 | 2026-09-22
PAV-ALM-00058 | BMS | Module | EESL-S03-P06-M03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-23 01:10 | 2026-09-23 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-09-23
PAV-ALM-00059 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-23 05:35 | 2026-09-23 05:50 | 15 | 73.4 | 68 | %RH | Cleared |  |  | 2026-09-23
PAV-ALM-00060 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-23 05:55 | 2026-09-23 06:25 | 30 | 72.5 | 68 | %RH | Cleared |  |  | 2026-09-23
PAV-ALM-00061 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-23 12:15 | 2026-09-23 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-09-23 12:37 | 2026-09-23
PAV-ALM-00062 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-23 13:30 | 2026-09-23 13:35 | 5 |  |  |  | Cleared | control-room | 2026-09-23 13:31 | 2026-09-23
PAV-ALM-00063 | PCS | Inverter | EESL-BESS-S03-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-24 02:35 | 2026-09-24 03:20 | 45 |  |  |  | Cleared |  |  | 2026-09-24
PAV-ALM-00064 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-24 05:40 | 2026-09-24 05:55 | 15 | 73.6 | 68 | %RH | Cleared |  |  | 2026-09-24
PAV-ALM-00065 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-24 07:35 | 2026-09-24 07:50 | 15 | 72.7 | 68 | %RH | Cleared |  |  | 2026-09-24
PAV-ALM-00066 | BMS | Pack | CONT-S03-01-PACK-04 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-09-24 18:25 | 2026-09-24 18:35 | 10 |  |  |  | Cleared |  |  | 2026-09-24
PAV-ALM-00067 | BMS | Module | EESL-S03-P06-M06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-25 01:55 | 2026-09-25 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-09-25 01:57 | 2026-09-25
PAV-ALM-00068 | PCS | Inverter | EESL-BESS-S03-PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-09-25 14:55 | 2026-09-25 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-09-25 14:56 | 2026-09-25
PAV-ALM-00069 | BMS | Cell | EESL-S03-P02-M01 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-09-26 03:15 | 2026-09-26 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-09-26 03:17 | 2026-09-26
PAV-ALM-00070 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-26 10:30 | 2026-09-26 10:40 | 10 |  |  |  | Cleared |  |  | 2026-09-26
PAV-ALM-00071 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-26 19:35 | 2026-09-26 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-09-26
PAV-ALM-00072 | PCS | Inverter | EESL-BESS-S03-PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-09-27 18:10 | 2026-09-27 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-09-27 18:11 | 2026-09-27
PAV-ALM-00073 | BMS | Module | EESL-S03-P03-M07 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-09-28 00:55 | 2026-09-28 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-09-28
PAV-ALM-00074 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-28 14:50 | 2026-09-28 15:05 | 15 | 31.794 | 30 | kW | Cleared | a.khan | 2026-09-28 14:53 | 2026-09-28
PAV-ALM-00075 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-09-28 17:35 | 2026-09-28 17:45 | 10 | 30.513 | 30 | kW | Cleared |  |  | 2026-09-28
PAV-ALM-00076 | BMS | System | EESL-BESS-S03 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-09-28 20:00 | 2026-09-28 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-09-28
PAV-ALM-00077 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-09-29 04:20 | 2026-09-29 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-09-29 04:28 | 2026-09-29
PAV-ALM-00078 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-09-29 04:50 | 2026-09-29 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-09-29 04:53 | 2026-09-29
PAV-ALM-00079 | PCS | Inverter | EESL-BESS-S03-PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-09-29 12:05 | 2026-09-29 12:35 | 30 |  |  |  | Cleared |  |  | 2026-09-29
PAV-ALM-00080 | EMS | Site Controller | EESL-BESS-S03-EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-09-29 12:15 | 2026-09-29 12:40 | 25 |  |  |  | Cleared |  |  | 2026-09-29
PAV-ALM-00081 | PCS | Inverter | EESL-BESS-S03-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-29 17:40 | 2026-09-29 17:50 | 10 | 1395.45 | 1500 | kVA | Cleared |  |  | 2026-09-29
PAV-ALM-00082 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-09-29 20:40 | 2026-09-29 21:40 | 60 |  |  |  | Cleared | control-room | 2026-09-29 20:48 | 2026-09-29
PAV-ALM-00083 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-09-30 08:55 | 2026-09-30 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-09-30
PAV-ALM-00084 | HVAC | HVAC Unit | EESL-BESS-S03-HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-09-30 09:35 | 2026-09-30 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-09-30
PAV-ALM-00085 | PCS | Inverter | EESL-BESS-S03-PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-09-30 18:40 | 2026-09-30 18:55 | 15 | 1453.005 | 1500 | kVA | Cleared |  |  | 2026-09-30