## Data
alarm_id | source_system | asset_type | asset_code | alarm_code | alarm_type | severity | severity_level | description | probable_cause | start_time | end_time | duration_min | trigger_value | threshold_value | unit | status | acknowledged_by | acknowledged_at | start_date
ALM-00001 | BMS | Pack | PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-01 15:50 | 2026-08-01 16:30 | 40 |  |  |  | Cleared |  |  | 2026-08-01
ALM-00002 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-01 22:10 | 2026-08-01 22:30 | 20 | 31 | 38 | degC | Cleared | j.mehta | 2026-08-01 22:16 | 2026-08-01
ALM-00003 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-02 18:35 | 2026-08-02 19:00 | 25 | 21.572 | 20 | kW | Cleared |  |  | 2026-08-02
ALM-00004 | PCS | Inverter | PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-03 04:00 | 2026-08-03 05:25 | 85 |  |  |  | Cleared |  |  | 2026-08-03
ALM-00005 | BMS | Pack | PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-03 08:30 | 2026-08-03 08:55 | 25 |  |  |  | Cleared |  |  | 2026-08-03
ALM-00006 | PCS | Inverter | PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-08-03 22:25 | 2026-08-03 22:30 | 5 | 53.067 | 50.2 | Hz | Cleared | s.iyer | 2026-08-03 22:26 | 2026-08-03
ALM-00007 | PCS | Inverter | PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-04 01:15 | 2026-08-04 01:30 | 15 | 45.95 | 80 | degC | Cleared |  |  | 2026-08-04
ALM-00008 | PCS | Inverter | PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-04 12:10 | 2026-08-04 12:25 | 15 |  |  |  | Cleared |  |  | 2026-08-04
ALM-00009 | BMS | System | BESS-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-04 21:10 | 2026-08-04 21:35 | 25 | 9.96 | 10 | % | Cleared | control-room | 2026-08-04 21:17 | 2026-08-04
ALM-00010 | BMS | Module | MOD-07 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-05 00:55 | 2026-08-05 01:00 | 5 | 7.7 | 40 | mV | Cleared |  |  | 2026-08-05
ALM-00011 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-05 14:50 | 2026-08-05 15:05 | 15 | 21.196 | 20 | kW | Cleared | a.khan | 2026-08-05 14:53 | 2026-08-05
ALM-00012 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-05 17:35 | 2026-08-05 17:45 | 10 | 20.342 | 20 | kW | Cleared |  |  | 2026-08-05
ALM-00013 | BMS | System | BESS-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-05 20:00 | 2026-08-05 20:40 | 40 | 10 | 10 | % | Cleared |  |  | 2026-08-05
ALM-00014 | BMS | Cell | MOD-01 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-06 03:15 | 2026-08-06 03:20 | 5 | 3.481 | 3.6 | V | Cleared | control-room | 2026-08-06 03:17 | 2026-08-06
ALM-00015 | EMS | Site Controller | EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-08-06 10:30 | 2026-08-06 10:40 | 10 |  |  |  | Cleared |  |  | 2026-08-06
ALM-00016 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-06 19:35 | 2026-08-06 19:40 | 5 | 52.4 | 68 | %RH | Cleared |  |  | 2026-08-06
ALM-00017 | BMS | Module | MOD-06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-07 02:25 | 2026-08-07 02:40 | 15 | 7.2 | 40 | mV | Cleared | m.rao | 2026-08-07 02:31 | 2026-08-07
ALM-00018 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-07 20:25 | 2026-08-07 21:25 | 60 | 0.019 | 50.15 | Hz | Cleared |  |  | 2026-08-07
ALM-00019 | BMS | Module | MOD-09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-08 00:35 | 2026-08-08 01:15 | 40 | 7.3 | 40 | mV | Cleared | m.rao | 2026-08-08 00:41 | 2026-08-08
ALM-00020 | BMS | Module | MOD-15 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-08 01:25 | 2026-08-08 01:35 | 10 | 6.9 | 40 | mV | Cleared |  |  | 2026-08-08
ALM-00021 | PCS | Inverter | PCS-01 | GROUND_FAULT | Isolation | Critical | 3 | Ground / insulation fault detected | Earth leakage on AC or DC side | 2026-08-08 05:10 | 2026-08-08 06:25 | 75 |  |  |  | Cleared | m.rao | 2026-08-08 05:23 | 2026-08-08
ALM-00022 | EMS | Site Controller | EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-08-08 11:05 | 2026-08-08 11:10 | 5 |  |  |  | Cleared | m.rao | 2026-08-08 11:07 | 2026-08-08
ALM-00023 | BMS | Module | MOD-09 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-08 17:35 | 2026-08-08 17:40 | 5 | 6.9 | 40 | mV | Cleared | s.iyer | 2026-08-08 17:36 | 2026-08-08
ALM-00024 | EMS | Site Controller | EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-08-09 09:35 | 2026-08-09 10:00 | 25 |  |  |  | Cleared | s.iyer | 2026-08-09 09:40 | 2026-08-09
ALM-00025 | PCS | Inverter | PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-08-10 01:30 | 2026-08-10 02:05 | 35 | 762.44 | 1000 | kVA | Cleared |  |  | 2026-08-10
ALM-00026 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-10 09:25 | 2026-08-10 10:40 | 75 | 31.43 | 38 | degC | Cleared | m.rao | 2026-08-10 09:58 | 2026-08-10
ALM-00027 | BMS | Cell | MOD-03 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-10 13:50 | 2026-08-10 15:25 | 95 | 3.468 | 3.6 | V | Cleared | m.rao | 2026-08-10 14:13 | 2026-08-10
ALM-00028 | EMS | Site Controller | EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-08-10 22:00 | 2026-08-10 22:05 | 5 |  |  |  | Cleared |  |  | 2026-08-10
ALM-00029 | PCS | Inverter | PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-11 02:45 | 2026-08-11 02:55 | 10 | 45.85 | 80 | degC | Cleared | m.rao | 2026-08-11 02:49 | 2026-08-11
ALM-00030 | BMS | Pack | PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-11 15:00 | 2026-08-11 17:00 | 120 |  |  |  | Cleared | j.mehta | 2026-08-11 15:29 | 2026-08-11
ALM-00031 | HVAC | HVAC Unit | HVAC-01 | LowCoolantFlow | Coolant | Alarm | 2 | Coolant flow below minimum | Pump degradation / air lock in loop | 2026-08-11 19:25 | 2026-08-11 20:10 | 45 | 22.488 | 30 | L/min | Cleared | control-room | 2026-08-11 19:43 | 2026-08-11
ALM-00032 | BMS | Module | MOD-04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-08-12 15:20 | 2026-08-12 15:45 | 25 | 30.17 | 44 | degC | Cleared | m.rao | 2026-08-12 15:29 | 2026-08-12
ALM-00033 | BMS | System | BESS-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-12 21:50 | 2026-08-12 21:55 | 5 | 9.94 | 10 | % | Cleared | a.khan | 2026-08-12 21:51 | 2026-08-12
ALM-00034 | PCS | Inverter | PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-13 02:35 | 2026-08-13 03:20 | 45 |  |  |  | Cleared |  |  | 2026-08-13
ALM-00035 | BMS | Pack | PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-13 18:25 | 2026-08-13 18:35 | 10 |  |  |  | Cleared |  |  | 2026-08-13
ALM-00036 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-14 08:55 | 2026-08-14 10:55 | 120 | 31.38 | 38 | degC | Cleared |  |  | 2026-08-14
ALM-00037 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-14 09:35 | 2026-08-14 09:40 | 5 | 52.5 | 68 | %RH | Cleared |  |  | 2026-08-14
ALM-00038 | PCS | Inverter | PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-08-14 18:40 | 2026-08-14 18:55 | 15 | 968.67 | 1000 | kVA | Cleared |  |  | 2026-08-14
ALM-00039 | BMS | System | BESS-01 | LowInsulation | Isolation | Critical | 3 | DC isolation resistance below threshold | Moisture ingress / insulation degradation in DC bus | 2026-08-15 22:20 | 2026-08-15 23:25 | 65 | 2142.636 | 2100 | kOhm | Cleared | m.rao | 2026-08-15 22:32 | 2026-08-15
ALM-00040 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-16 07:50 | 2026-08-16 08:20 | 30 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-08-16
ALM-00041 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-17 08:10 | 2026-08-17 08:15 | 5 | 0.02 | 50.15 | Hz | Cleared |  |  | 2026-08-17
ALM-00042 | PCS | Inverter | PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-17 12:25 | 2026-08-17 12:40 | 15 |  |  |  | Cleared |  |  | 2026-08-17
ALM-00043 | BMS | Module | MOD-13 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-17 17:05 | 2026-08-17 17:10 | 5 | 9.1 | 40 | mV | Cleared |  |  | 2026-08-17
ALM-00044 | BMS | Module | MOD-04 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-08-17 18:15 | 2026-08-17 18:25 | 10 | 33.11 | 44 | degC | Cleared | a.khan | 2026-08-17 18:19 | 2026-08-17
ALM-00045 | BMS | Module | MOD-09 | HighCellTemp | Thermal | Alarm | 2 | Cell temperature above warning threshold | Local hot-spot; reduced coolant flow to module | 2026-08-17 18:25 | 2026-08-17 19:05 | 40 | 32.74 | 44 | degC | Cleared | a.khan | 2026-08-17 18:43 | 2026-08-17
ALM-00046 | BMS | Module | MOD-03 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-18 01:10 | 2026-08-18 01:25 | 15 | 8.7 | 40 | mV | Cleared |  |  | 2026-08-18
ALM-00047 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-18 12:15 | 2026-08-18 13:00 | 45 | 0.091 | 50.15 | Hz | Cleared | m.rao | 2026-08-18 12:37 | 2026-08-18
ALM-00048 | HVAC | HVAC Unit | HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-08-18 13:30 | 2026-08-18 13:35 | 5 |  |  |  | Cleared | control-room | 2026-08-18 13:31 | 2026-08-18
ALM-00049 | EMS | Site Controller | EMS-01 | SETPOINT_DEVIATION | Dispatch | Warning | 1 | Delivered power deviates from setpoint | Ramp-rate limit / SOC headroom curtailed dispatch | 2026-08-19 02:50 | 2026-08-19 03:05 | 15 | 20.295 | 20 | kW | Cleared | a.khan | 2026-08-19 02:55 | 2026-08-19
ALM-00050 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-19 15:10 | 2026-08-19 15:25 | 15 | 0.021 | 50.15 | Hz | Cleared |  |  | 2026-08-19
ALM-00051 | BMS | System | BESS-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-19 23:15 | 2026-08-20 | 45 | 9.99 | 10 | % | Cleared | j.mehta | 2026-08-19 23:17 | 2026-08-19
ALM-00052 | BMS | Pack | PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-20 09:35 | 2026-08-20 09:40 | 5 |  |  |  | Cleared |  |  | 2026-08-20
ALM-00053 | HVAC | HVAC Unit | HVAC-01 | HighHumidity | Humidity | Warning | 1 | Enclosure humidity above limit | Dehumidification lag during warm humid period | 2026-08-20 22:10 | 2026-08-20 22:50 | 40 | 50.4 | 68 | %RH | Cleared |  |  | 2026-08-20
ALM-00054 | EMS | Site Controller | EMS-01 | DISPATCH_REJECTED | Dispatch | Alarm | 2 | Market/operator dispatch could not be met | Insufficient available energy for requested discharge | 2026-08-21 04:20 | 2026-08-21 05:05 | 45 |  |  |  | Cleared | s.iyer | 2026-08-21 04:28 | 2026-08-21
ALM-00055 | EMS | Site Controller | EMS-01 | FREQ_EXCURSION | Grid | Warning | 1 | Grid frequency outside deadband | System frequency event; regulation dispatch triggered | 2026-08-21 04:50 | 2026-08-21 05:00 | 10 | 0.025 | 50.15 | Hz | Cleared | s.iyer | 2026-08-21 04:53 | 2026-08-21
ALM-00056 | PCS | Inverter | PCS-01 | COMM_FAULT | Comm | Warning | 1 | PCS controller communication fault | Modbus/EtherCAT frame loss to plant controller | 2026-08-21 12:05 | 2026-08-21 12:35 | 30 |  |  |  | Cleared |  |  | 2026-08-21
ALM-00057 | EMS | Site Controller | EMS-01 | PRICE_STALE | Market | Info | 0 | Market price feed stale | Delayed price telemetry from market operator | 2026-08-21 12:15 | 2026-08-21 12:40 | 25 |  |  |  | Cleared |  |  | 2026-08-21
ALM-00058 | PCS | Inverter | PCS-01 | OVERLOAD | Current | Warning | 1 | Apparent power near/above rating | Reactive dispatch stacked on high active power | 2026-08-21 17:40 | 2026-08-21 17:50 | 10 | 930.3 | 1000 | kVA | Cleared |  |  | 2026-08-21
ALM-00059 | HVAC | HVAC Unit | HVAC-01 | CompressorFault | Mechanical | Alarm | 2 | Compressor trip / fault | High discharge pressure cut-out; compressor restart | 2026-08-21 20:40 | 2026-08-21 21:40 | 60 |  |  |  | Cleared | control-room | 2026-08-21 20:48 | 2026-08-21
ALM-00060 | BMS | Module | MOD-06 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-22 01:55 | 2026-08-22 02:15 | 20 | 7.1 | 40 | mV | Cleared | s.iyer | 2026-08-22 01:57 | 2026-08-22
ALM-00061 | PCS | Inverter | PCS-01 | OVERFREQUENCY | Grid | Alarm | 2 | Grid frequency above ride-through band | Grid disturbance; frequency-watt response engaged | 2026-08-22 14:55 | 2026-08-22 15:05 | 10 | 54.141 | 50.2 | Hz | Cleared | control-room | 2026-08-22 14:56 | 2026-08-22
ALM-00062 | BMS | Cell | MOD-06 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-24 04:55 | 2026-08-24 05:20 | 25 | 3.472 | 3.6 | V | Cleared |  |  | 2026-08-24
ALM-00063 | BMS | Cell | MOD-16 | HighCellVoltage | Voltage | Alarm | 2 | Cell voltage exceeded charge limit | Over-charge / weak cell during high-SOC charging | 2026-08-24 12:55 | 2026-08-24 13:55 | 60 | 3.472 | 3.6 | V | Cleared | control-room | 2026-08-24 13:06 | 2026-08-24
ALM-00064 | BMS | Module | MOD-08 | CellImbalance | Voltage | Warning | 1 | Cell voltage imbalance above warning threshold | Cell-to-cell SOC divergence; balancing lag near top of charge | 2026-08-24 17:00 | 2026-08-24 17:25 | 25 | 8.5 | 40 | mV | Cleared |  |  | 2026-08-24
ALM-00065 | BMS | System | BESS-01 | SOC_Limit | SOC | Warning | 1 | Pack SOC reached operating limit | Deep discharge into evening peak / full after overnight charge | 2026-08-24 22:15 | 2026-08-24 22:30 | 15 | 9.96 | 10 | % | Cleared | s.iyer | 2026-08-24 22:20 | 2026-08-24
ALM-00066 | PCS | Inverter | PCS-01 | IGBT_OVERTEMP | Thermal | Alarm | 2 | IGBT junction temperature high | High load coincident with elevated ambient; derated cooling | 2026-08-25 18:10 | 2026-08-25 18:15 | 5 | 59.91 | 80 | degC | Cleared | s.iyer | 2026-08-25 18:11 | 2026-08-25
ALM-00067 | EMS | Site Controller | EMS-01 | SCADA_COMM_LOSS | Comm | Critical | 3 | Loss of comms to plant SCADA | Network outage between EMS and site controller | 2026-08-26 18:50 | 2026-08-26 19:05 | 15 |  |  |  | Cleared | a.khan | 2026-08-26 18:57 | 2026-08-26
ALM-00068 | BMS | Pack | PACK-01 | BMSCommWarning | Comm | Warning | 1 | Intermittent BMS internal communication fault | CAN bus noise / slave BMU handshake retry | 2026-08-27 03:20 | 2026-08-27 03:35 | 15 |  |  |  | Cleared | s.iyer | 2026-08-27 03:21 | 2026-08-27
ALM-00069 | HVAC | HVAC Unit | HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-08-27 07:25 | 2026-08-27 08:05 | 40 | 95 | 150 | Pa | Cleared |  |  | 2026-08-27
ALM-00070 | HVAC | HVAC Unit | HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-08-27 17:20 | 2026-08-27 17:40 | 20 | 94 | 150 | Pa | Cleared | a.khan | 2026-08-27 17:24 | 2026-08-27
ALM-00071 | HVAC | HVAC Unit | HVAC-01 | HighCoolantTemp | Coolant | Alarm | 2 | Coolant return temperature above limit | Cooling demand exceeded capacity at peak ambient | 2026-08-29 20:55 |  |  | 31.33 | 38 | degC | Active | j.mehta | 2026-08-29 21:11 | 2026-08-29
ALM-00072 | HVAC | HVAC Unit | HVAC-01 | FilterClog | Airflow | Warning | 1 | Air-filter differential pressure high | Filter fouling; service due | 2026-08-30 08:35 | 2026-08-30 08:50 | 15 | 101 | 150 | Pa | Cleared | m.rao | 2026-08-30 08:36 | 2026-08-30